## Slide 1: PDCWG Report to ROS
August 12, 2010
Sydney Niemeyer

## Slide 2: In This Report
PDCWG August 11 meeting items.
ERCOT Frequency Control Performance.
  CPS, RMS1 through July 2010.
Update on Governor setting changes and impact on frequency profile.
  Does it cost more to have a smaller governor dead band?
June 23, 2010 DCS event Interconnection Primary Frequency Response detail.

## Slide 3: PDCWG Meeting August 11, 2010
Nodal 24 hour LFC test review:
  Regulation deployments utilize CPS 1 control strategy. Is this appropriate for a single Balancing Authority Interconnection?
  QSE performance
    GREDP
    QSE AGC strategy
Review July 2010 Frequency Events.
Wind Generator Primary Frequency Response implementation.

## Slide 4: PDCWG Meeting August 11, 2010 continued
BAL-001-TRE-1 update on next draft posting.
  LCRA, Eric Armke developing a manual on using the Resource performance evaluation tool.
Frequency Event review.
  June 23, 2010 15:20 DCS event Primary Frequency Response evaluation completed.
  White paper review and discussion.

## Slide 5
CPS1 = 161.13

## Slide 8
of ERCOT Frequency

## Slide 10
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 147.04

## Slide 11
2008 First 7 months

## Slide 12
Single 600 MW unit MW movement due to frequency.

## Slide 13: 600 MW Generator Governor Change
Protocol and Guide settings:
  5% droop curve that steps to the 5% droop curve at the dead-band.
  Allows up to +/-0.036 Hz dead-band.
Change Governor settings
  5% droop curve that is a straight line function from the dead-band.
  Decrease Governor Dead-band from:
    +/-0.036 Hz to +/-0.01666 Hz

## Slide 14: Status as of August 5, 2010
Units with Governors presently set with an intentional deadband less than or equal to +/-0.01666 Hz and droop curve with no step function.
  14,137 MW Total Capacity Identified by PDCWG members.
    1690 MW Lignite
    5534 MW Coal
    3780 MW Combustion Turbine Combined Cycle
    1519 MW Combustion Turbine Simple Cycle
    1224 MW Steam Turbine – natural gas fired
    240 MW Hydro
    150 MW Wind Generators

## Slide 16
Same 600 MW unit MW movement due to frequency each year.

## Slide 17: Benefits of Governor Change
Generators move 24.38% less with lower dead-band compared to larger dead-band and poorer frequency control.
Less maintenance on Generators.
Generators are more stable due to fewer and smaller MW fluctuations.
Grid is more reliable due to higher probability that frequency will be near 60 Hz at the time of a major event.
Generators perform better during events since they are more stable before the event occurs.
Potential fuel and emission savings.

## Slide 18: June 23, 2010 DCS Event
Initial (Point B) Primary Frequency Response -486.77 MW/0.1 Hz.
Sustained (Point B+30 second) Primary Frequency Response -416.33 MW/0.1 Hz.
Average Primary Frequency Response -458.85 MW/0.1 Hz.
Decreased performance at Point B+30 seconds due to 14,000 MW of combustion turbine operating at HSL.
  As turbine speed decreases with frequency, the mass flow through the turbine decreases causing MW output to decrease.
  Approximately 90 MW of total output was lost causing frequency to decay from 59.775 Hz to 59.740 Hz.
  This is a normal condition of combustion turbines operating at the exhaust temperature limit of the turbine (HSL). Grid operators should be aware of this situation. In this scenario, if reserves are exhausted frequency would continue to decline instead of stabilizing.
Primary Frequency Response Evaluation

## Slide 19
Generation Change -475 MW after 1253 MW tripped (net). PFR from governors = 778 MW
243 MW of LaaR Tripped (Load acting as a Resource)
252 MW of Load Dampening due to low frequency.
778 MW Pri Freq Response from Gen
246 MW of LaaR Response
252 MW of Load Dampening
1275 MW total Response.
1253 MW Tripped
22 MW error (load dampening, load growth or other data error)
June 23, 2010 DCS Event

## Slide 20
Poorer
Better
Secondary frequency decline.

## Slide 21
688 MW Pri Freq Response from Gen
246 MW of LaaR Response
339 MW of Load Dampening
1273 MW total Response.
1253 MW Tripped
22 MW error (load dampening, load growth or other data error)
Approximately 90 MW output loss from combustion turbines operating at exhaust temperature limit when mass flow decreased during low frequency.
Approximately 14,000 MW of combustion turbines operating at HSL.
339 MW of Load Dampening due to new lower frequency.
Adequate reserves returned frequency to 60 Hz.