ERCOT Operations Report

Jul 2010 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 07/02/2010 01:44:48 | 59.816 | 79 | Unit trip with 674 MW |
| 07/06/2010 20:30:08 | 59.817 | 103 | Unit trip with 796 MW |
| 07/10/2010 04:10:53 | 59.850 | 34 | Unit trip with 626 MW |
| 07/12/2010 13:17:12 | 59.838 | 84 | Unit trip with 795 MW |
| 07/12/2010 13:54:41 | 59.827 | 143 | Unit trip with 630 MW |
| 07/14/2010 14:08:08 | 59.898 | 7 | Unit trip with 192 MW. Out of Up Reg |
| 07/20/2010 07:25:04 | 59.805 | 122 | Unit trip with 810 MW |
| 07/26/2010 04:55:32 | 59.877 | 8 | Unit trip with 740 MW |
| 07/26/2010 05:09:44 | 59.800 | 84 | Unit trip with 783 MW |
| 07/27/2010 15:56:01 | 59.834 | 60 | Unit trip with 690 MW |
| 07/30/2010 14:31:16 | 59.836 | 88 | Unit trip with 770 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 7/2/10 1:44:47 | 7/2/10 2:08:34 | 0:23:47 | 821.7 |  |
| 7/5/10 11:07:57 | 7/5/10 11:18:10 | 0:10:13 | 346.85 | Large SCE change |
| 7/6/10 20:30:11 | 7/6/10 20:49:18 | 0:19:07 | 816.41 |  |
| 7/10/10 4:10:55 | 7/10/10 4:27:26 | 0:16:31 | 640.33 |  |
| 7/11/10 1:01:27 | 7/11/10 1:11:02 | 0:09:35 | 352.19 | Unit Trip |
| 7/12/10 1:47:22 | 7/12/10 2:03:50 | 0:16:28 | 341.52 | Out of Up Reg. |
| 7/12/10 13:17:15 | 7/12/10 13:36:38 | 0:19:23 | 704.35 |  |
| 7/12/10 13:54:39 | 7/12/10 14:17:46 | 0:23:07 | 768.39 |  |
| 7/14/10 14:08:07 | 7/14/10 14:34:01 | 0:25:54 | 384.20 |  |
| 7/20/10 7:25:02 | 7/20/10 7:48:53 | 0:23:51 | 880.44 |  |
| 7/26/10 4:55:29 | 7/26/10 5:07:36 | 0:12:07 | 496.26 |  |
| 7/26/10 5:09:45 | 7/26/10 5:41:51 | 0:32:06 | 907.1 |  |
| 7/27/10 15:56:03 | 7/27/10 16:27:14 | 0:31:11 | 725.7 |  |
| 7/27/10 18:27:05 | 7/27/10 18:34:54 | 0:07:49 | 352.2 | Unit Trip |
| 7/27/10 22:35:12 | 7/27/10 22:52:02 | 0:16:50 | 330.8 | Out of Up Reg |
| 7/30/10 14:31:15 | 7/30/10 14:56:51 | 0:25:36 | 715 |  |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | RMR | Total |
| --- | --- | --- | --- | --- | --- | --- |
| DFW | 39 | 4 | 8 | 12 | 0 | 51 |
| Houston | 1 | 8 | 2 | 10 | 0 | 11 |
| Western | 0 | 2 | 3 | 5 | 6 | 11 |
| Corpus | 1 | 3 | 0 | 3 | 0 | 4 |
| Northeast | 0 | 0 | 4 | 4 | 0 | 4 |
| North | 0 | 0 | 1 | 1 | 1 | 2 |
| Austin | 0 | 0 | 1 | 1 | 0 | 1 |
| E RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| San Antonio | 0 | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| South | 0 | 0 | 0 | 0 | 0 | 0 |
| Bryan Area | 0 | 0 | 0 | 0 | 0 | 0 |
| Laredo | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 41 | 17 | 19 | 36 | 7 | 84 |

| Historical Totals | Jul-10 | Jul-09 | Jun-10 |
| --- | --- | --- | --- |
| Austin | 0 | 5 | 0 |
| Bryan Area | 0 | 0 | 0 |
| Corpus | 4 | 0 | 0 |
| DFW | 43 | 28 | 64 |
| E RIO | 0 | 9 | 4 |
| Houston | 9 | 37 | 6 |
| Laredo | 0 | 0 | 0 |
| North | 1 | 46 | 9 |
| Northeast | 0 | 2 | 0 |
| San Antonio | 0 | 14 | 2 |
| South | 0 | 13 | 0 |
| W RIO | 0 | 0 | 0 |
| Western | 8 | 19 | 18 |
| Total | 65 | 173 | 103 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Matador - Paducah Claire St. 69KV | Aspermont - Spur 138KV | 21 |
| Watermill - West Levee - Sargent Road 345KV | Duncanville South - Cedar Hill 138KV | 10 |
| Green Bayou - Gable & Hardy - Crockett 138KV | Garrott - Midtown 138KV | 9 |
| Meadow - PH Robinson 345 KV | North Alvin - Hastings 138KV | 9 |
| Sandow Switch - Austrop 345KV | Round Rock - Round Rock Northeast 138KV | 9 |
| Graham - Parker 345KV | Leon Switch - Flat Creek 138KV | 5 |
| Zorn - Marion - Clear Springs 345KV | Clear Springs 345/138KV T1 AT | 4 |
| Hamilton - Sonora 138KV | Sonora - Friess Ranch 69KV | 4 |
| Jack County - Reno 138KV | Bridgeport TU - Wise County 138KV | 4 |
| Olney - Westover 69 KV | Elbert Switch to Seymour. | 4 |
| Zorn - Lytton Springs & Austrop 345KV | McCarty Lane - Redwood 138KV | 4 |
| Fort Bend - East Bernard 138KV | Flewellen - Peters 138KV | 3 |
| Ingleside Cogen Switch - Oxychem Corpus Christi 138KV | Ingleside - DuPont PP2 138KV | 3 |
| Odessa EHV 345/138Kv Auto #2 | Odessa EHV 345/138Kv Auto #1 | 3 |
| Sherry Switch - Hanley SES - Executive Parkway 138KV | Sherry Switch - Park Row 138KV | 3 |
| Holly - Barney Davis 138KV | Airline - Cabaniss 138KV | 2 |
| Hutto - Gilleland Creek 138KV | Round Rock - Round Rock Northeast 138KV | 2 |
| Desoto Switch - Cedar Hill TU 138KV | Desoto Switch - Parkerville Road 138KV | 2 |
| McDonald - Spraberry SW138KV | Stanton East - Midland East 138KV | 1 |
| Jack County - Reno 138KV | Bridgeport TU - Bridgeport Tap 138KV | 1 |
| Greens Bayou 345/138KV At #1 | Greens Bayou 345/138KV At #2 | 1 |
| Marion - Skyline - Elm Creek 345KV | Schertz - Parkway 138KV | 1 |
| Midland East - Odessa EHV 345KV | Odessa EHV 345/138KV AT #1 | 1 |
| Roanoke Switch - Euless - Saginaw Switch 138KV | Roanoke Switch - Roanoke West 138KV | 1 |
| Sandow Switch - Temple Switch 345KV | Hearne 138/69KV AT | 1 |
| Snyder - Sun Switch 138KV | Morgan Creek - Sun Switch 138KV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West – North | 11 |
| North – Houston | 6 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 07/01/2010 | Transmission and Security Desk V4 Rev15 | 480 |
| 07/01/2010 | Shift Supervisor Desk V4 Rev 15 | 479 |
| 07/01/2010 | Frequency Control Desk V4 Rev 14 | 478 |
| 07/01/2010 | Day-Ahead Desk V4 Rev 12 | 477 |

## Blackout/Load Shed Incidences

None

EEA

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

None

Communication

None

## ERCOT peak (Unofficial)

07/16 17:00 60,425 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2007 | 2008 | 2009 | 2010 |
| January | 4.55 | 3.30 | 4.11 | 3.78 |
| February | 3.75 | 3.59 | 3.49 | 3.79 |
| March | 2.70 | 3.29 | 3.24 | 2.24 |
| April | 3.00 | 2.45 | 2.66 | 2.47 |
| May | 3.22 | 3.01 | 2.90 | 2.63 |
| June | 4.46 | 2.81 | 2.89 | 2.84 |
| July | 4.29 | 2.55 | 2.83 | 2.39 |
| August | 3.11 | 3.66 | 3.07 | NA |
| September | 3.78 | 4.99 | 3.68 | NA |
| October | 3.08 | 2.79 | 2.92 | NA |
| November | 2.95 | 2.60 | 1.93 | NA |
| December | 3.74 | 4.54 | 3.70 | NA |
| Annual Average | 3.55 | 3.29 | 3.11 | 2.88 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 7/1/10 | 0:15 | 8:00 | Advisory issued for Hurricane Alex. |
| 7/5/10 | 16:05 | 19:00 | Advisory issued due to ARRS below 3000 MW. |
| 7/17/10 | 15:50 | 18:15 | Advisory issued for ARRS below 3000 MW. |
| 7/19/10 | 16:08 | 19:11 | Advisory issued for ARRS below 3000 MW. |
| 7/21/10 | 7:28 | 10:50 | OCN issued for a projected reserve capacity shortage for hours ending 14:00 - 18:00 |
| 7/30/10 | 15:00 | 19:35 | Advisory issued due to ARRS below 3000 MW. |

Transmission Watch

7/06 09:30	Transmission Watch issued due to forced outage at Gails substation.  Implemented Block Load Transfer up to 2 MW from ERCOT (Gails substation) to SPP (Draw substation).

7/07 00:15	Transmission Watch issued due to forced outage at Gails substation.  Implemented Block Load Transfer up to 2 MW from ERCOT (Gails substation) to SPP (Draw substation).

Emergency Notice

7/01 18:00	Issued a Market Emergency Notice.  Replacement Reserve Service (RPRS) did not meet the time requirement for operating day 07/02/2010.

Texas RE Event Analysis

7/01 18:00	Market Emergency Notice issued for RPRS market delay.

Others

None