###### ERCOT STEADY STATE WORKING GROUP

###### PROCEDURES

ERCOT STEADY-STATE WORKING GROUP’S SCOPE

The ERCOT Steady-State Working Group (SSWG) operates under the direction of the Reliability and Operations Subcommittee (ROS). The SSWG’s main objectives are to produce seasonal and future load-flow base cases, coordinate tie-line data, maintain the ERCOT Data Dictionary, , prepare data for and review seasonal transmission loss factor calculation, and provide requested transmission system data and power-flow support documents to market participants. Some of the above responsibilities are further described as follows:

- Many of the responsibilities of the working group meet certain NERC Reliability Standards

- Develop and maintain load-flow base cases for the spring, summer, fall, and winter seasons of the upcoming year. The cases, collectively known as Data Set A, are produced by the SSWG on an annual basis. These seasonal cases consist of one on peak and one off-peak case for each of the four seasons.

- Develop and maintain load-flow base cases for the five future years following the upcoming year. The cases, collectively known as Data Set B, are produced by the SSWG on an annual basis. These future cases consist of five summer on-peak cases, and one minimum case.

- Maintain and update the ERCOT Data Dictionary to reflect new bus information and SCADA names.

- Review the Steady-State Working Group portion of the ERCOT Planning Guides and propose changes as needed

- Prepare data for and review seasonal transmission loss factor calculation on an annual basis.

- Coordinate tie-line data submission to ERCOT with neighboring companies.

- Update the SSWG base cases quarterly.Maintain and update the contingencies files.

###### SECTION 1.0 – Data Requirements

1.1 GENERAL

    - Model

# The network model submitted by the TSP shall be in a format compatible with the latest approved PSS/E and rawd ASCII data format based on a 100 MVA base. The model should reflect expected system operation.

    - Data

The SSWG will use loads based upon the load data in the ERCOT Annual Load Data Request (ALDR) to build two sets of cases, Data Set A and Data Set B (see Sections 2.1 and 2.2).

Data Set A consists of seasonal cases for the following year.  Data Set B consists of the following:

- Future summer peak planning cases

- A future minimum load planning case

After completion of the Data Set B cases, the following data will be updated by the SSWG:

- ERCOT Data Dictionary

- Updated Contingency List

1.2 BUS DATA

    - Areas defined by TSP

Each TSP is assigned a unique area name and number

    - Bus Data Records

All in-service transmission (60kV and above) and generator terminals shall be modeled in load-flow cases. Fixed reactive resources shall be modeled as a fixed component in the switchable shunt data record and not be part of the bus record.

    - Bus Ranges

Presently, ERCOT is modeled within a 100,000-bus range. The Chairman of the SSWG allocates bus ranges, new or amended, with confirmation from the SSWG members.  Bus ranges are based on high-side bus ownership. (Refer to TSP Bus/Zone Range Table in Appendix A)

Bus numbers from within the TSP’s designated bus range are assigned by the TSP and are to remain in the assigned ranges until the equipment or condition that it represents in the ERCOT load-flow cases changes or is removed.

    - Zone Ranges

Presently the Chairman of the SSWG allocates zone ranges, new or amended, with confirmation from SSWG members. Each TSP represents their network in the ERCOT load-flow cases using allocated zone ranges. Zone numbers that have been assigned by the TSP, within the TSP’s designated zone range, may be changed by the TSP as needed to represent their network in the ERCOT load-flow cases. Every zone number assigned must be from the TSP’s designated zone range.

    - Owner IDs

    - Bus Name

Electrical Bus names shall not identify the customers or owners of loads or generation at new buses unless requested by customers.  The twelve characters Electrical Bus Name representing individual transmission element in the planning model shall be unique and follow certain technical criteria as stated in the ERCOT Nodal Protocol Section 3.10.

1.3 LOAD DATA

Each bus modeling a load must contain at least one load data record.    All loads (MW and MVAR) should be modeled on the high side of transformers serving load at less than 60 kV.

Guidelines:

    - The bus number in the load data record must be a bus that exists in the base case. All self-serve loads must be identified by “SS”. If there are multiple self-serve loads at the same bus, then the self-serve loads will be identified by S1, S2, S3, etc.  Partial self-serve load should be modeled as a multiple load with “SS” identifying the self-serve portion. Distributed generation must be identified by “DG” and modeled as negative load.

    - The load data record zone number must be in the zone range of the TSP serving the load.  It does not have to be the same zone that the bus is assigned to.

1.3.3	Generator auxiliary load should not be modeled at generating station buses.

1.3.4	In conformance to NERC Planning Requirements and the ERCOT Operating Guides Section 5.1.2, Entities not having representation on SSWG shall submit the data to ERCOT or if the directly connected TDSP has agreed to be the agent on SSWG for that entity, to that TSP.  If load data is not timely submitted on the schedule and in the format defined by the TSP, then ERCOT shall calculate loads based on historical data and insert these loads into the load flow cases during DataSetA and DataSetB annual updates.

    - Multiple loads from different TSPs at a bus may be used. At this time, each TSP can define a load however it wishes with a load ID of its choice though careful coordination is required between TSP representatives to ensure that the loads at the bus get modeled correctly.

1.4 GENERATOR DATA

    - Acquisition of Generator Data

Only net real and reactive generator outputs and ratings should be modeled in load-flow cases. Net generation is equal to the gross generation minus station auxiliaries and other internal power requirements.  All non-self-serve generation connected at 60kV and above with at least 10 MW aggregated at the point of interconnect must be explicitly modeled. A generator explicitly modeled must include generator step-up transformer and actual no-load tap position. Generation of less than 10 MW is still required to be modeled, but not explicitly.

Unit reactive limits (leading and lagging) for existing units should be obtained from the most recent generator reactive unit test data provided by ERCOT. For units that have not been tested, limits will be obtained from the generator owner. Unit reactive limits (leading and lagging) are tested at least once every two years (ERCOT Protocols, Section 6.10.3.5 and ERCOT Operating Guides, Section 6.2.3). If the test does not meet these requirements, reference the ERCOT Operating Guides for further explanation or actions. Note that the CURL MVAr values are gross values at the generator terminals. Limited ERCOT RARF data shall be made available to SSWG upon request.

Generator reactive limits should be modeled by one value for Qmax and one value for Qmin as described below:

Qmax

Qmax is the maximum net lagging MVAr observed at the low side of the generator step up transformer when the unit is operating at its maximum net dependable MW capability.

Qmin

Qmin is the maximum leading MVAr observed at the low side of the generator step up transformer when the unit is operating at its maximum net dependable MW capability.

      - Self-Serve Generation

Total self serve generation MWs shall match total self-serve load MWs.

      - Coordination with other ERCOT Working Groups

All generator data should be coordinated with the Dynamics Working Group, OWG, Network Data Support Working Group and System Protection Working Group members to assure that it is correct before submitting the cases. This will insure that all of the cases have the most current steady state and dynamics information.  The following are items from the fall peak SSWG case that should be provided to these working groups for annual coordination by the end of the year:

- Unit bus number

- Unit ID

- Unit maximum and minimum real power capabilities

- Unit maximum and minimum reactive power capabilities

- Unit MVA base

- Resistive and reactive machine impedances

- Resistive and reactive generator step-up transformer impedances

    - Generation Dispatch Methodology

In order to simulate the future market, the following methodology for generation dispatch has been adopted for building the Data Set A and Data Set B load flow cases.

Existing and planned units owned by the Non-Opt-In Entities (NOIE) are dispatched according to the NOIE's planning departments; unless a NOIE requests that their units are to be dispatched according to the order that is described below.

Private network generation is also dispatched independently. The plants are dispatched to meet their load modeled in the case. DC Ties are modeled as load levels or at generation levels based on historical data.  Likewise, wind plants are modeled at generation levels based on historical data.

See Appendix I on Method for Calculating Wind Generation Levels in SSWG Cases.

Units that are solely for black start purposes are to be modeled in the base cases; however, these units should not be dispatched.  Black start units are designated with a unit ID that begins with the letter ‘B’ which can be followed by an alphanumeric character (for example, ‘B1’, ‘B2’, etc.).

All other units are dispatched by performing a system simulation using the UPLAN software package.  The UPLAN simulation will dispatch units in order to minimize production costs taking into account unit start-up times and cost and heat rates while adhering to the following guidelines for each set of cases:

Data Set A cases are dispatched to maintain CSC and CRE loading below their limits.  The Uplan software simulates the system load for the two weeks leading up to the peak hour for each season.

Data set B economically constrained cases are dispatched in the most economical way for a given load level with no consideration for overloads.  The Uplan software  simulates the system load for the two weeks leading up to the peak hour for each summer peak case and the two weeks leading up to the minimum load hour for the minimum case.

In all cases spinning reserve is maintained according to ERCOT guides.  Mothballed units are treated as described in Appendix F.  The dispatch may be modified for Data Set A cases if necessary to maintain voltages at acceptable levels.

Once ERCOT receives an executed interconnection agreement or public, financially-binding agreement between the generator and TSP under which generation interconnection facilities would be constructed or a commitment letter from a municipal electric provider or an electric cooperative building a generation project, the project will be included in the base cases beyond its expected in-service year.

SSWG shall be able to review and modify the generation dispatch based on historical information.

Extraordinary Dispatch Conditions

Future cases may not include sufficient dispatchable generation resources to match load.  When such a condition is encountered in future cases, ERCOT may increase generation resources by taking the indicated action, or adding generation, in the following order:

- DC ties dispatched to increase transfers into ERCOT to the full capacity of the DC ties.

- Mothballed units that have not announced their return to service.

- Ignore spinning reserve.

- Increase NOIE generation with prior NOIE consent

- Add publicly announced plants without interconnect agreements.

- Black start Units

- Add generation resources at the sites of retired units.

1.5 LINE DATA

    - Use of Load-flow Data Fields

      - Circuit (Branch) Identifier

Circuit identifiers are limited to two alphanumeric characters.  Each TSP will determine its own naming convention. These identifiers are typically numeric values (e.g. 1 or 2) that indicate the number of branches between two common buses, but many exceptions exist.

      - Impedance Data

The resistive and reactive impedance data contained in the load-flow cases are both expressed in per-unit quantities that are calculated from a base impedance. The base impedance for transmission lines is calculated from the system base MVA and the base voltage of the transmission branch of interest.  The system base MVA used in the ERCOT load-flow cases is 100 MVA (S = 100 MVA).  The base voltage for a transmission line branch is the nominal line-to-line voltage of that particular transmission branch

        - Charging

Line charging is expressed as total branch charging susceptance in per unit on the 100 MVA system base.  The total branch charging is expressed in MVARs and divided by the system base MVA to get per unit charging.

      - Facility Ratings

ERCOT load-flow cases contain fields for three ratings for each branch record.  The ratings associated with these three fields are commonly referred to as Rate A, Rate B and Rate C.  Following are the ERCOT facility ratings definitions:

        - Ratings Definitions

Rate A – Normal Rating

Continuous Rating:  Represents the continuous MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer (MLSE) at the applicable ambient temperature.   The Transmission Facility can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

Rate B – Emergency Rating

Emergency Rating:  Represents the two (2) hour MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer (MLSE) at the applicable ambient temperature.  The Transmission Facility can operate at this rating for two (2) hours without violation of NESC clearances or equipment failure.

Rate C – Conductor/Transformer Rating

Emergency Rating of the Conductor or Transformer:  Represents the two (2) hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The conductor or transformer can operate at this rating for two (2) hours without violation of NESC clearances or equipment failure.

I.e. Rate C ≥ Rate B ≥ Rate A

      - Status

Entities are allowed to submit branch data with an out-of-service status for equipment normally out of service.

      - Line Length and Ownership

The line length will be submitted by the TSP’s during the DSA and DSB case creation and TPIT updates and ownership may be submitted at their discretion.

        - Line Length

This data will be provided in miles

    - Coordination of Tie Lines

Careful coordination and discussion is required among SSWG members to verify all modeled tie-line data.

    - Metering Point

Each tie line or branch must have a designated metering point and this designation should also be coordinated between neighboring TSP areas.

1.6 TRANSFORMER DATA

    - Transformer Data

Every transformer is to be represented in the transformer data record block.  Both two winding transformers and three winding transformers can be specified in the transformer data record block. Three-winding transformer should be represented by its three-winding model and not by its equivalent two-winding models.

      - Bus Numbers

      - Transformer Circuit Identifier

Where practical, TO’s should identify autotransformers with the letter A as the first character of the ID field.  Generator Step-Up transformers should be identified with the letter G.  Phase-shifting transformers should be identified with the letter P.

      - Impedance Data

The resistance and reactance data for transformers in the load flow database are specified: (1) in per-unit on 100 MVA system base (default), (2) in per-unit on winding base MVA and winding bus base voltage, (3) in transformer load loss in watts and impedance magnitude in per-unit on winding base MVA and winding bus base voltage.

        - Resistance

Transformer test records should be used to calculate the resistance associated with a transformer branch record. Where transformer test records are unavailable, the resistance should be entered as zero.

        - Reactance

Transformer test records or transformer nameplate impedance should be used to calculate the reactance associated with a transformer branch record. Where the transformer resistance component is known, the transformer impedance is calculated on the same base using the known data and the reactance component is determined using the Pythagorean Theorem. Where the transformer resistance is assumed to be zero, the calculated transformer impedance can be assumed to be equal to the transformer reactance.

        - Susceptance

For load-flow modeling purposes, the transformer susceptance is always assumed to be zero.

      - Transformer Ratings

The ratings used for transformer branches are defined the same as in Section 1.5.1.4, Facility Ratings.

1.7 STATIC REACTIVE DEVICES

Presently all shunt reactors and capacitors that are used to control voltage at the transmission level are to be modeled in the ERCOT load-flow cases to simulate actual transmission operation.

    - Switched Shunt Devices

      - Bus Shunt

A shunt capacitor or reactor connected to the high side or low side of a substation transformer in a substation should be represented in the ERCOT load-flow case as a switched or fixed shunt device to accurately simulate operating conditions.

###### SECTION 2.0 – Load-Flow Procedures and Schedules

2.1 DATA SET A CONSIDERATIONS

    - Data Set A Uses

Data Set A cases are submitted by the ERCOT region in response to FERC 715 requirements and are posted on ERCOT web site for general use.

    - Data Set A Case Definitions

Load-flow cases produced by ESP are to be divided into two groups.  The first group, “Data Set A,” models expected conditions for the following year’s four seasons (eight cases).  The second group, “Data Set B,” models cases for the five-year planning horizon.

Data Set A seasons are as follows:

SPG		March, April, May

SUM		June, July, August, September

FAL		October, November

WIN		December, January, February

ERCOT DATA SET A BASECASES

(YR) = FOLLOWING YEAR

| BASE CASE | NOTES | TRANSMISSION IN-SERVICE DATE |
| --- | --- | --- |
| (YR) SPG1 | 2 | April 1, (YR) |
| (YR) SPG2 | 3 | April 1, (YR) |
| (YR) SUM1 | 1 | July 1, (YR) |
| (YR) SUM2 | 3 | July 1, (YR) |
| (YR) FAL1 | 2 | October 1, (YR) |
| (YR) FAL2 | 3 | October 1, (YR) |
| (YR+1) WIN1 | 1 | January 1, (YR+1) |
| (YR+1) WIN2 | 3 | January 1, (YR+1) |

## Notes

- Cases to represent the maximum expected load during the season.

- Cases to represent maximum expected load during month of transmission in-service date.

- Cases to represent lowest load on same day as the corresponding seasonal case (not a minimum case). For example, (YR) FAL2 case represents the lowest load on the same day as the (YR) FAL1 case.

    - Entity Responsibilities

The Data Set A load-flow cases are assembled and produced by ESP.  The responsibilities for providing this data are divided among the various market participants. These data provision responsibilities may overlap among the various market participants because participants may designate their representative or a participant may be a member of more than one market participant group.  The market participants can generally be divided into four groups: TSPs, Load Serving Entities, Power Generating Companies, and Marketing Entities.  The data responsibilities of each group are as follows:

      - TSPs

It is the responsibility of the TSPs to provide all the data required to model the transmission system (line impedances, ratings, transformers, reactive sources, etc.) This will include data for all generator step-up transformers physically tied to the system of the TSP.  Transmission providers shall model the load or generation data if they are the designated representatives for load entities or power generating companies.

      - Load Serving Entities

Each ERCOT DSP directly interconnected with the transmission system (or its agent so designated to ERCOT) shall provide annual load forecasts to the ERCOT as outlined in the ERCOT Annual Load Data Request (ALDR) Procedures.  For each substation not owned by either a TSP or a DSP, the owner shall provide a substation load forecast to the directly connected TDSP sufficient to allow it to adequately include that substation in its ALDR response.  Entities not having representation on SSWG shall submit the data to ERCOT or if the directly connected TDSP has agreed to be the agent on SSWG for that entity, to that TSP.  If load data is not timely submitted on the schedule and in the format defined by the TSP, then ERCOT shall calculate loads based on historical data and insert these loads into the load flow cases during DataSetA and DataSetB annual updates.

      - Power Generating Companies

It is the responsibility of the generation entities to provide all data required to model the generators in all the cases. See Section 1.4. This data should be coordinated with ERCOT and should include but is not limited to unit capabilities.

      - Marketing Entities

It is the responsibility of marketers to supply the load and/or generation data if they are the designated representatives for either a load or generating entity or both.

2.2 DATA SET B CONSIDERATIONS

    - Data Set Uses

    - Data Set B Case Definitions

ERCOT DATA SET B BASECASES

(YR) = FOLLOWING YEAR

| BASE CASE | NOTES | TRANSMISSION IN-SERVICE DATE |
| --- | --- | --- |
| (YR+1) SUM1 | 1 | JULY 1, (YR+1) |
| (YR+2) SUM1 | 1 | JULY 1, (YR+2) |
| (YR+3) MIN | 2 | JANUARY 1, (YR+3) |
| (YR+3) SUM1 | 1 | JULY 1, (YR+3) |
| (YR+4) SUM1 | 1 | JULY 1, (YR+4) |
| (YR+5) SUM1 | 1 | JULY 1, (YR+5) |

## Notes

- Cases to represent the maximum expected load during the season.

- Cases to represent the absolute minimum load expected for (YR+3).

    - Data Set B Dispatching

Data Set B will contain economically dispatched generation (ECO).

    - ERCOT Data Dictionary

| Each SSWG member will submit a data file listing all buses that exist in any case from either Data Set A or B 30 days after completion of Data Set B cases. This file is called the ERCOT Data Dictionary. The data dictionary is used by ESP to show correlation between base case bus numbers and TSP area SCADA names. Also, the data dictionary without the SCADA names is included as part of ERCOT’s FERC 715 filing. |  |  |  |
| --- | --- | --- | --- |

2.3

    - Case Updates

When necessary the TSP will document updates, which will be posted by ESP. The file name should have a clear description, which will include provider’s acronym and the specific case to be updated.

SECTION 3.0 – Other SSWG Activities

3.1 TRANSMISSION LOSS FACTOR CALCULATIONS

Transmission Loss Factors

The transmission loss factors must be calculated according to Protocol Section 13. The loss factors are calculated using SSWG DSA base cases.

3.2	Planning-Related Contingency Database

Contingency Procedure:

- All the TO’s either submit the contingencies individually or will updated the existing database.

- The duplicate contingencies are included only once and are attributed to the TO which comes first in alphabetical order.

- All contingencies need to be categorized based on NERC categories.

- Current contingency database is sent to all TSP’s for reviewing.

- ERCOT will update the contingency database when a TSP submits the contingency changes related to a major Topology change ( - incremental change).Every time the database changes, files in MUST, PSS/E, Powerworld, UPLAN and VSAT formats are posted online.

- Detailed instructions can be found on the Planning and Operations Information website at ercot.com.

APPENDICES

Appendix B

Glossary of Terms

ALDR	Annual Load Data Request

BUS	A node representing point of electrical connection, such as substation or radial tap point.

CSC	Commercially Significant Constraint

ECO	Economically Dispatched

ERCOT	Electric Reliability Council of Texas

ESP	ERCOT System Planning

IPP	Independent power producer

LSE	Load serving entity

LTC	Load tap changing transformer

MLSE	Most limiting series element

MSL	Multi-section line

NERC	North American Electric Reliability Corporation

NESC	National Electric Safety Code

NOIE	Non-opt-in Entity

NUG	Non Utility Generator

PUCT	Public Utility Commission of Texas

QSE	Qualified Scheduling Entity

REP	Retail Electric Provider

SSWG	Steady State Working Group

TPIT	Transmission Project Information Tracking

TSP	Transmission Service Provider

VCRP	Voltage control and reactive planning

Zone	A predefined sub-system within a load-flow case.

MOD 	Model on Demand

IMM	Information Model Manager

Appendix H

Transmission Element Naming Convention

ERCOT Nodal Protocol (Section 3.10 Network Operations Modeling and Telemetry) requires consistency among various network models including Annual Planning Models, CRR Network Models and Network Operating Models.  One of the requirements requests the name of existing Transmission Elements including Electrical Buses, lines, transformers, generators, loads, breakers, switches, capacitors, reactors, phase shifters, or other similar devices, if modeled as part of the ERCOT Transmission Grid, in these three models must be identical and shall be unique within all of ERCOT.  ERCOT SSWG and NDSWG have coordinated their efforts to develop the Transmission Element Naming Convention standard.  The naming convention standard is in three parts but constitutes one standard.  At the present, only the Electrical Bus names in Part 1 is applicable to SSWG’s Annual Planning Models.

Part 1: Electrical Busses Names

The 12 characters Electrical Bus Name representing the same Transmission Element shall be identical in the Network Operations Model, Updated Network Operations Model, Annual Planning Model and CRR Network Model and shall be unique within all of ERCOT.

The following technical requirements must be followed:

- Name shall only include uppercase alpha-numeric values (A to Z and 0 to 9),

- The only special character allowed is the underscore (“_”)

- No spaces are allowed except at end of the name, and

- Names must be unique.

The following points are recommended, but are not requirements:

- Names should be derived from the substation name,

- All Electrical Bus Names within a substation should be related,

- A unique voltage designator should be within the Name, and

- A TSP prefix should be used to avoid naming conflicts.

Part 2: Lines, Breakers and Switches Names

Transmission Breakers and Switches representing the same Transmission Breaker or Switch in the Network Operation Model, Updated Network Operations Model, and CRR Network Model shall be unique within the same substation and shall have the first 14 characters unique.

All other Transmission Elements representing the same Transmission Element in the Network Operation Model, Updated Network Operations Model, and CRR Network Model shall have the first 14 characters unique within the Transmission Element type within all of ERCOT.

Part 3: Substation Names

Substation names representing the same substation in the Network Operation Model, Updated Network Operations Model, and CRR Network Model shall be unique for all substations within ERCOT and shall be limited to 8 characters.

END OF DOCUMENT

# Comments

“Powerflow” or “Loadflow”; there is no consistency in this document when referring to our base cases.

There is no ERCOT MLSE Database.  Each TSP maintains their own database which must be provided to ERCOT upon request.  Already a NERC requirement.

Assume this would go away or should be replaced with ‘update SSWG information manual’ or whatever it’s called.

Informational in nature

We need a binding dispatch section, but it doesn’t need to be right here

Informational in nature

Not needed anymore

Informational in nature

Remove since it is already a NERC requirement

Is this necessary?

What is this?

Does SSWG perform studies or just build models?

In recent years, there has been no request for SSWG to provide analytical support beyond providing modeling data for general purpose use.  Individual TSPs and other groups in ERCOT actually perform the analysis.

Our principal charges seem to include providing N-0 secure base cases, tracking projects, and providing transmission loss factor calculations.

SSWG ensures N-0 security in the base cases.  The voltage Profile group ensures N-1 security for real time operations.  There is no working group in ERCOT that analyzes regional voltage and reactive needs.

This statement does not seem to apply anymore, since this is performed by the voltage profile group or individual TSPs.

Nodal - This doesn’t apply anymore and should be removed.

Informational in nature

Got as far as this point at 7/22/2010 PLWG meeting.

Nodal - Owner IDs will automatically be generated by TP.

Nodal – DG is modeled as a generator, not a load.  Would always have  to adjust by PMCR.

No need to duplicate Op Guide Section 5.1.2.  Reword to point to 5.1.2.

Nodal – Needs further discussion about how reactive limits will be set in the cases

Informational in nature

Informational in nature

Nodal – Update reflecting how PUN data gets to SSWG or TSPs

See note above.

Information contained in other parts of the Planning Guide.  Maybe should be changed to tell how that data gets to SSWG.

ERCOT to review? TSPs to review?  Seems self-evident.

More discussion may be necessary.  Are binding requirements needed for setting voltage profile.

Do not need this in Planning Guides.

This should probably be addressed elsewhere in the Planning Guides.

Not needed.

Informational in nature.

Nodal – Ownership will automatically be assigned through TP.

Informational in nature.

Informational in nature.

Nodal – Tie lines in NMMS contain information from both TSPs and TP combines those into one branch model and applies the lowest ratings.

Informational in nature.

Informational in nature.

Informational in nature.

Nodal – The method for tie line submission is entirely different, assuming SSWG uses TP raw output, and there is no coordination needed.

Informational in nature.

Informational in nature.

Informational in nature.

Informational in nature.

Informational in nature.

Informational in nature.

Informational in nature.

Nodal – CSC determination does not use DSA cases.

Delete and replace with much more generic wording.

This section is incomplete and does not cover data in columns B-I of the Data Dictionary.  Pull out the ‘Reference_Tab_Data_Dictionary’ tab from the actual data dictionary for section to include in Planning Guides.

See note above

Seems like these requirements would be covered elsewhere in ERCOT Network Modeling information.

Delete and replace with much more generic wording.

The ALDR information will come from ERCOT

While good practice, these should not be made binding requirements.

My feeling is that while these are important to creating a proper case, they probably do not need to be binding requirements.

Informational in nature

Informational in nature

Informational in nature

This should be deleted and moved to a “Readme” tab in the contingency database.  An NPRR would be needed anytime new columns need to be added.

Per Woit this appendix is candidate to be included on the ERCOT web site under planning information.

Send TSP Bus/Zone range to ercot.com as a separate file and reference the name and location in planning guides.

This should not be included for the same reason as the Zone tables below.

Save table at ercot.com and reference name and location in planning guides.

These Zone tables do not need to be included in Planning Guides.  Do not want to have to submit a PGRR to change Zone name. Save table at ercot.com and reference name and location in planning guides.

Seems like another part of the Guides would contain a glossary of terms, but this might need to stay if not.

Per NERC Standards, TDSPs must provide ERCOT with Line Rating Methodology upon request. These methodologies could be posted on the ERCOT web site Planning area.

This does not belong in the Planning Guides.  I would think an SSWG informational document, non-binding in nature, would be the ideal location for this information.

Informational in nature.

ERCOT is providing the TPIT information for the Planning Guides.

Either condense and/or move in its entirety to an appendix on ercot.com.

This does not belong in the Planning Guides.  I would think an SSWG informational document, non-binding in nature, would be the ideal location for this information.

Either condense or delete and/or move this section to ercot.com

After discussion with Woitt recommend moving to the ERCOT web site under planning.

Informational in nature.

Either condense or delete and/or move section to ercot.com

After discussion with Woitt recommend moving to the ERCOT web site under planning.

Informational in nature.