## DAM Issues List
Issue # | Issue Title | Contingency & Overload Pair (Date Observed) | DSV | Date Submitted | Submitter | Category | Mkt. | Priority | Issue Description | Assigned To | Status | Estimated Resolution Date | Comments
5 | Total Energy Sold/Purchase & PtP |  |  | 2010-06-11 | LUME | Reports | DAM | 1 | The DAM Total Energy Purchased and DAM Total Energy Sold reports don't include awarded PtP Obligations and Options. To fulfill the Protocol requirements of 4.5.3 (2) (f-g) all energy purchased and sold at each Settlement Point in the DAM, including PTP obligations should be included in these reports or in an alternative report(s). Seperately, another report that describes those NOIE CRRs options not redeemed in the DAM and held as an option into Real Time is needed. | Mereness | Pending Report | ? | [ERCOT 8/12/2010] Mereness asked team to create prototype- single DAM Awards report with column layout: (See Sample DAM Report Worksheet in this workbook) DAMDate Hour SettPt EnergySold (Sum cleared: 3PSO + EOnlyOffers) PtPObligations Source cleared CRR-Source (NOIE CRR Offers minus cleared) EnergyPurchased (Sum cleared of Energy Bids) PtPObligations Sink cleared CRR-Sink (NOIE CRR Offers minus cleared)
6 | Hutto - Round Rock NE 138 kV Line Rating | DAUSGAR5 1660__C HUTTO 138 RRNES 138 (07/31/10), DHUTGIL8 1660__C HUTTO 138 RRNES 138 (08/10/10) | 21 | 2010-07-30 | LUME | Ratings Error | DAM | 1 | In the DAM results for 7/31/10, the Hutto – Round Rock NE 138 kV Line bound every hour of the day with a reported line rating of 237 MVA (likely a dynamic line rating). Both the SSWG planning case for summer 2010 and the ERCOT Transmission Project Information Tracking (TPIT) database indicate that this line was just rebuilt in June 2010 for 326 MVA nominal rating. | John Adams | Line Ratings Issue | ? | LUME believes that this may be an issue where the Nodal Operations model has not been updated and is still showing the old line rating. Please research this, notify us of your findings, and update the model as appropriate. [ERCOT 8/5/2010] the current DSV where this will be corrected is DSV 24 [LUME 8/10/10] why shouldn't this incorrect line rating be fixed in EMS and all inflight NMMS model builds ASAP? [ERCOT 8/11/10] Ratings on line 1660_C from Hutto to Round Rock NE have been updated to 326/326/368. DSV 22-Aug18
8 | Congestion on Cedar Crest - Compton 69 kV line | SCDHSOR8 3890__A CDCSW 69 CMPST 69 (06/15/10), SINDCDC8 3890__A CDCSW 69 CMPST 69 (07/31/10) SCMPIND8 3890__A CDCSW 69 CMPST 69 (08/13/10) SCMPIND8 3890__A CDCSW 69 CMPST 69 (08/15/10) |  | 2010-06-15 | LUME | Misc. Error | DAM | 1 | This line is modeled on a radial-feed in both the SSWG cases and the Operations load flow model, and therefore should not overload under contingency conditions. | sai | Active |  | ERCOT researched this and found that it was an incorrect contingency definition and invalid load throw over constraint had been identified as the root cause and had been fixed (reported at 7/29 NATF mtg). Issue still shows up in 7/31/10 DAM. When will Network model get corrected? [ERCOT 8/6/2010] Can luminant provide the contingency name and overloaded element as it appears in the DAM reports. With the contingencies being auto-generated and the name not beig consistent till DSV22 - it is going to be a challenge to track and confirm if contingencies are being correctly defined. For DAM OD 7/31 - it appears that the contingency in question is SINDCDC8 and this caused the overload of 69 KV line 3890_A from cedar hill to sorcey road. [LUME 8/10/10] the contingency causing this overload in the DAM for 7/31/10 was Industrial Blvd - Cedar Crest Sw. 138 kV line [ERCOT 8/12/10] Has not re-occurred since 7/31/10, but continue to monitor [LUME 8/16/10] This constraint was active again on 8/13 & 8/15, so it is still an active issue
9 | Congestion on Seguin - Seguin West | DMARZOR5 428T428_1 SEGUIN 138 SEGUWE 138 (05/21/10), DCLEZOR5 428T428_1 SEGUIN 138 SEGUWE 138 (07/15/10), DMARZOR5 428T428_1 SEGUIN 138 SEGUWE 138 (08/04/10) | 21 | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Fayette, Gideon, Hays, Lost Pines, & Rio Nogales (see 7/19/10 NATF presentation for more detail) | sai | Active | ? | Between 5/21 & 7/15, bound 27 days in Nodal and 3 days in Zonal. It is unclear whether this is a model quality problem or simply a difference in how Nodal flows will differ from Zonal. LUME developing RAP for ERCOT consideration. [LUME 8/12/10] - between 5/21/10 and 8/11/10, this line has constrained on 51 seperate days. We continue to believe that there is something counterintuitive going on in the Nodal DAM model in this area that needs to be better understood and corrections made as appropriate. [ERCOT 8/15/2010] For DAM OD 7/13 the cause of the high shadow price was due to incorrect contingency SCDHSOR8 couple with a load rollover scheme that resulted in a high radial load pocket on this contingency. For DAM OD 8/11. constraint SEGUIN 138.0 SEGUWE 138.0 under contingency SSMIMCQ8: SSMIMCQ8 is a single line outage contingency. The outage element is the line from SMI to MCQUEE. The overloading line is the line from SEGUIN to SEQUWE with large shadow price. Once the line from SMI to MCQUEE is out, the line from SEGUIN to SEQUWE becomes a radial line that serves the loads SMI_T8, SEGUWE_SEGUWET1 , SEGUWE_SEGUWET2, SMI_SMI_T7, SMI_SMI_T1, SMI_SMI_T6, CAPERP_CATERPT2, and CATERP_CATERPT1. Thus for this binding constraint, only LZ_LCRA and LZ_SOUTH has nozero shfit factors -- the sum of LDF of individual loads. Analyzing other cases to determine of overload. [LUME 8/16/10] What DAM model corrections need to occur to correct the modeling issues described by ERCOT for the 8/11/10 DAM (see ERCOT's 8/15/10 comments)? Additionally, does ERCOT have an explanation of what is causing the XMAR58 (8/13/10), DMARZOR5 (8/13 & 8/15), and SSHEMAR8 (8/17) constraints to result in overloads of this line?
10 | Congestion on Round Rock - Round Rock NE | DHUTGIL8 1660__A RRNES 138 RNDRK 138 (07/21/10) |  | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Sandow (see 7/19/10 NATF presentation for more detail). LUME submitted 3 RAPs to ERCOT/Oncor for consideration on 7/14/10 | John Adams | Active | ? | Between 6/18 & 7/15, bound 7 days in Nodal and 15 days in Zonal. This seems like a legitimate constraint that is binding on a repeated basis and consistent with the directives in Section 3.10.4 (6) of the Nodal Protocols, may benefit from additional operational intervention or system monitoring while longer term line upgrades are pursued. 8/5/2010 - RAPs received at ERCOT - under review (still under review-JA)
11 | Congestion on Mc Neil - Summit | SMCNMAG8 CKT_907_1 MCNEIL 138 SUMMIT 138 (07/17/10) |  | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Sandow (see 7/19/10 NATF presentation for more detail) | sai | Active | ? | Between 5/12 & 7/15, bound 17 days in Nodal and 0 days in Zonal. It is unclear whether this is a model quality problem or simply a difference in how Nodal flows will differ from Zonal. LUME developing RAP for ERCOT consideration [ERCOT 8/6/2010] As per ERCOT analysis presented at NATF - did not find any network model issues. However the DAM dispatch is quite different from Zonal RT dispatch. Suspect due to offer/bid submission patern for Nodal DAM. [LUME 8/10/10] Can ERCOT please offer some supporting analytical evidence that the principle cause of the dramatically higher flows reported on this line at the 7/29/10 NATF meeting are indeed due to odd offer / bid submission by performing analysis such as was presented at the 8/5/10 Nodal DAM Deep Dive for the Pearsall - Derby constraint?
14 | Congestion on Victoria - N. Victoria 138 kV line | SVICMAG9 N_VICT_VICTOR1_1 VICTORIA 69 N_VICT 69 (07/17/10) |  | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/19/10 NATF presentation for more detail) | John Adams | Active | ? | Between 5/4 & 7/15, bound 12 days in Nodal and 0 days in Zonal. ERCOT has a MP in place in Zonal to control overloads on this line. How can this MP be reflected in DAM to provide a comparable treatment of this congestion management in Nodal DAM and RT as Zonal RT?
15 | Congestion on Trinidad - Winkler 138 kV line | SJEWPLS8 1240__K TRSES 138 WINKLER 138 (07/17/10), XJEW58 1240__K TRSES 138 WINKLER 138 (08/10/10) | 21 | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting North Load Zone (NLZ) to North Hub spreads (see 7/19/10 NATF presentation for more detail). RARF update to mark this load as self serving | ken ragsdale | Model Updates | ? | Between 5/4 & 7/15, bound 12 days in Nodal and 0 days in Zonal. ERCOT and LUME identified at the 7/29/10 NATF meeting that this is and 'end-to-end' line loading problem associated with an improper load distribution to the load serving busses along this line that contains Big Brown startup / standby load that should not be placed on this line. What needs to be done to get this corrected in the Nodal Model? Change Load to be zero in RARF- issues still to discuss versus systemic (psuedo measurement for SE)
16 | Congestion on Ennis Creek 138/69 kV auto | BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/13/10) BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/14/10) BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/15/10) BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/16/10) BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/17/10) | 21 | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting West Load Zone (WLZ) to West Hub spreads (see 7/19/10 and 7/29/10 NATF presentations for more detail) | sai | Pending Closure - Radial Load Pockets | ? | Between 6/5 & 7/15, bound 16 days in Nodal and 0 days in Zonal. ERCOT identified and reported at the 7/29/10 NATF meeting that this is issue is being caused by an improper breaker status in the Nodal model that is shown as closed, which is shown as open in Zonal. What needs to be done to get this corrected in the Nodal Model? [ERCOT 8/11/2010] ONCOR confirmed the breaker status is normally closed. The only equipment that is normally open is line 6765_D and both Nodal and Zonal databases are the same. PI data also shows flows and no outages on the 138/69kv transformer from 6/5 to 7/15. Base case violations on the Ennis creek 138/69 KV auto is showing frequently in the DAM runs. The cause is that this transformer is feeding a radial load pocket and the normal rating of this transformer is 24 MVA. The two radial loads LDF are OK (compared to PI data). Also, it appears that TSP confirmed that the rating of this transformer are correct 24/28. One additional piece of information is that the lines at the 69 KV are rated at nearly twice the transformer rating. Based on this information – this issue can be closed? [LUME 8/16/10] Between 6/5/10 and 8/17/10, this constraint has bound on 31 different days in the DAM and has accumulated >$71M of congestion, does ERCOT have any explanation for what is causing this chronic congestion associated with a Basecase (N-0) overload? [Dive Mtg 8/17] - Although issue associated with Radial Load pocket- desire to ensure that is the only issue since it is binding every day, and up to $17 million in cong costs
19 | Congestion on Odessa North - Odessa Basin 69 kV line | SPBSPB28 6915__A ODNTH 69 ODBSW 69 (07/31/10) |  | 2010-07-29 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting West Load Zone (WLZ) to West Hub spreads (see 7/29/10 NATF presentation for more detail) | ? | Contingency Issue | ? | [ERCOT 8/5/2010] Bad contingency definition. This constraint is under contingency 'SPBSPB28', new from DSV 20. System operations confirmed the definition are not correct. This contingency has been excluded by both EMS and MMS since 8/3 [LUME 8/12/10] - this line last showed up in the DAM on 8/4/10 (i.e. one day after the fix outlined above was implemented). Please confirm that there is some reasonable explanation for its occurrence after the fix was in place. Perhaps the correction to the model occurred late on 8/3/10 after the 8/4/10 DAM was already complete. Just wanting to make sure that this issue has truly been corrected. [ERCOT 8/12/2010] SPB5PBS8 and SSD5SDS8 single circuit contingencies have been removed from the model in DSV 22 (Scheduled NPROD date of 8/18/2010).
20 | Bennett Rd. - Decartur Tap 138 kV Line Rating | SJACREN8 910__D BNTSW 138 DCRTP 138 (07/30/10) |  | 2010-07-29 | LUME | Ratings Error | DAM | 1 | Congestion on this line seems to be negatively impacting Barton Chapel, Graham, Oklaunion, and WF Cogen (see 7/29/10 NATF presentation for more detail) | ? | Line Ratings Issue | ? | Luminant Energy understands that Oncor has identified that the correct static rating for this line is 186 MVA rather than 124 MVA and will be filing a NOMCR to correct this. [ERCOT 8/5/2010] Additional analysis information. 1. This congestion are negatively impacting Barton Chapel Wind Farm, Graham, Oklaunion, and WF Cogen. 2. Th wind resource offer negative EOCs. 3. Resources EMSES_UNIT1, EMSES_UNIT2 and EMSES_UNIT3 with negative shift factors were not availble for DAM. [LUME 8/10/10] What is the update on getting the incorrect line rating fixed? [ERCOT 8/11/10] Ratings updated to 214/214/229. NOMCR submitted on 7/29/2010 with an Energization date of 8/7/2010. NOMCR included in DSV22 (Scheduled NPROD date of 8/18/2010).
21 | Decartur Tap - Rhome 138 kV Line Rating |  |  | 2010-07-29 | LUME | Ratings Error | DAM | 1 | Congestion on this line seems to be negatively impacting Barton Chapel, Graham, Oklaunion, and WF Cogen (see 7/29/10 NATF presentation for more detail) | ? | Line Ratings Issue | ? | Luminant Energy understands that Oncor has identified that the correct static rating for this line is 186 MVA rather than 124 MVA and will be filing a NOMCR to correct this. [ERCOT 8/5/2010] Additional analysis information. 1. This congestion are negatively impacting Barton Chapel Wind Farm, Graham, Oklaunion, and WF Cogen. 2. Th wind resource offer negative EOCs. 3. Resources EMSES_UNIT1, EMSES_UNIT2 and EMSES_UNIT3 with negative shift factors were not availble for DAM. [LUME 8/10/10] What is the update on getting the incorrect line rating fixed? [ERCOT 8/12/2010] ERCOT has not yet received a NOMCR from ONCOR to correct these ratings. Sent an email to ONCOR requesting them to provide an update.
22 | Congestion on Elkton 345/138 kV auto | DTRCELK5 ELKTN_MR3L ELKTN 1 ELKTN 138 (08/10/10) DTRCELK5 ELKTN_MR3L ELKTN 1 ELKTN 138 (08/12/10) DTRCELK5 ELKTN_MR3L ELKTN 1 ELKTN 138 (08/13/10) DTRCELK5 ELKTN_MR3H ELKTN 345 ELKTN 1 (08/16/10) DTRCELK5 ELKTN_MR3L ELKTN 1 ELKTN 138 (08/16/10) | 21 | 2010-07-29 | LUME | Modeling | DAM | 1 | Congestion on this auto appears to be caused by a double element contigency (N-2) that is not a valid double-circuit contigency per Oncor (see 7/29/10 NATF presentation for more detail) | ? | Contingency Issue | ? | Lumiant Energy understands that Oncor is in agreement that an incorrect double-circuit contingency defintion (DTRCELK5 - Martin Lake - Tyler Grande / Elkton - Forney) is being used and will be filing a NOMCR to correct this [ERCOT 8/5/2010]: same popped up during LFC test on 8/4. online correction was made to EMS. Need to confirm future DSV releases have fixed this issue. [ERCOT 8/11/2010] The double circuit contingencies DFORFRN5 and DELKMLS5 have been removed by ERCOT/AG in NOMCR 6443_1 set to energize on 8/14/2010. DSV23- 9/1/10 [LUME 8/16/10] According to our research of the DSV21 contingency definition file: * DTRCELK5 (Martin Lake - Tyler Grande / Elkton - Forney) continues to be an invalid double circuit contingency and needs removed ASAP * DFORFRN5 (Forney Sw. - Forney Power Partners Dbl. Ckt.) is an invalid double circuit contingency in that it is only 0.10 miles long (i.e. < 0.5 mile criteria for valid dbl. ckt.) and needs to be removed ASAP * DELKMLS5 (Martin Lake - Elkton / Martin Lake - Tyler Grande) is a valid double circuit contingency and should not be removed from the contingency definition [Dive mtg 8/17] - ERCOT to provide details/confirmation for Martin Lake area contingencies
24 | Congestion on Wolf Hollow - Rocky Creek 345 kV line | S_2127 152__A WOFHO 345 RKCRK 345 (07/10/10) |  | 2010-07-29 | LUME | Modeling | DAM | 1 | Congestion on this line seems to be negatively impacting Comanche Peak and Wolf Hollow (see 7/29/10 NATF presentation for more detail) | ? | Model Updates | ? | The contigency S_2063 is a single line outage between CPSES and PKRSW [LUME 8/12/10] - This line has constrained 11 different time between 7/27/10 and 8/12/10 (10 different DAM days - sometimes for multiple contingencies in a day). The two contingencies associated with this overload have been Comanche Peak - Parker (S_2063) and Comanche Peak - Johnson Sw. (S_2127). What is seems especially confusing about these constraint pairs being binding, is that all of our offline studies show substantial amounts of spare export margin (~650 MW to 780 MW) from Comanche Peak for these two contingencies when associated with overloads of Wolf Hollow - Rocky Creek. In our offline planning studies the Contingency outage of the Comanche Peak - Decordova 345 kV line associated with overloads of Wolf Hollow - Rocky Creek indicate that the export margin from Comanche Peak is only ~50 MW (i.e. much more constraining than the two constraints listed above); however, this overload pair hasn't yet shown up in the Nodal DAM. [ERCOT 8/12/2010] DAM OD 7/28: The base case flow on this outage line is 848MW at hour 17. The base case flow on the line from WOFOH ( Wolf Hollow) to RKCRK (Rocky Creek) is 818MW. The redispatch is binding the line constraint from WOFOH to RKCRK: The dominant drivers of the flow are: 1. A large PTP source at the settlement point CPSES_UNIT1 with 1216MW and another large PTP source at the settlement point CPSES_UNIT2. They are two expensive PTP bid at 500$ and they are all fully loaded. Represent the outputs of the two large nuclear units CPSES_UNIT1 and CPSES_UNIT2 ?. These two units do not participate the DAM. The shfit factor for these two units are 0.393. 2. The CC plant WHCCS_CT1 at configuation WHCCS_CC1_2. Its mw schedule is 369MW and its shift factor is 0.47 3. The CC plant TEN_CC1 at configuration TEN_CC1_1. Its mw schedule is 196 MW and its shfit factor is 0.1. Comanche Peak & Wolf Hollow are located at the sending end of the binding constraint with shadow price of 90$ at hour 17. Since CPSES and WOFOH have significant postive shift factor, their LMP will be brought down by this shadow price. [LUME 8/16/10] ERCOT's technical description on 8/12/10 of what is happening in the DAM regarding the primary units that have a loading impact on this constraint all make sense from a shift factor perspective; however, what doesn't make sense is why Wolf Hollow - Rocky Creek is constraining associated with the SCPSPKR5 and SJONCPS5 contingencies in the first place rather than the SDCSCPS5 (Comanche Peak - Decordova 345 kV line) contingencies. A deep dive by LUME into the PSS/E cases prepared by Sia Moorty for 8/4/10, reveal that the Comanche Peak - Decordova 345 kV line is effectively missing from the case (i.e. their is a radial 345 kV line from Comanche Peak - Decordova that doesn't connect to anything at Decordova). This missing line appears to be the root cause of the unexplained Wolf Hollow - Rocky Creek 345 kV line congestion. [Dive mtg 8/17) - Continue research with Oncor and Resource Entity, and after confirming issue determine whether there is quality check to prevent errors.
25 | Congestion on Tenaska - Concord 138 kV line | STENGDV8 TEN_CRD2_1 TEN 138 CRD 138 (07/21/10) |  | 2010-07-29 | LUME | Modeling | DAM | 1 | Congestion on this line seems to be negatively impacting Tenaska Cleburne (see 7/29/10 NATF presentation for more detail) | ? | Pending Closure | ? | [ERCOT 8/5/2010] No issues found with network model. There are two lines between Tenaska and Conord: TEN_CRD1_1 and TEN_CRD2_1. The contigency is to out the line TEN_CRD2_1. [LUME 8/12/10] - overloads on this line have bound on 26 different days in the Nodal DAM trials between 6/30/10 and 8/10/10 and is negatively impacting the Tenaska Cogen plant in a way that is inconsistent with what has been observed in Real Time. Lumn talking with Tenaska- may lower and eventually remove [ERCOT 8/12/2010] DAM OD 7/28 The contigency definition of S_1089 is: There are two lines between Tenaska and Conord: TEN_CRD1_1 and TEN_CRD2_1. The contigency is to out the line TEN_CRD2_1. The binding constraint is at the line TEN_CRD1_1. The base case flow on these two lines are 92MW and 180MW, respectively. S_1089 TEN_CRD1_1 TEN 138.0 CRD 138.0 Using Hour 17 as an example, the dominant contributors to the post-contigency flow are: TEN_CC1_1 with 196MW, an energy only offer at settlement point TEN_CT1_STG with 100MW, and a PTP bid source at the same settlement point TEN_CT1_STG with 100MW. The total injections of these three control variable are 400MW. The shift factor for these three resources is 0.759. Since the binding contigency constraint shadow price is about 30 $. With shfit factor of 0.759, the binding constraint itself can bring down the LMP at TENASKA by 30*0.759 = 24 $. Since HB LMP is average of 345kv hub bus LMP and the constraint is at 138KV, LMP at TENASKA is lower than HB_NORTH LMP. [DIve mtg- 8/17] - Chronic congestion that is not sensible- ERCOT asked if same bid/offer being submitted that is overloading day-after-day
26 | Numerous Line Rating Questions (see separate tab) |  |  | Various | LUME | Ratings Error | DAM | 1 | Various lines that have shown up as overloaded elements during congestion have materially different ratings than either the Network Model or the Planning Model indicating that their may be a ratings error in one or more of these models that needs verified | ? | Line Ratings Issue | Some ratings have already been resolved. More detailed tracking of these coming soon | Details in Old_Rating_Issues tab
28 | Adverse impact on DAM performance due to large number of CRR Offers |  |  |  | ERCOT | Market Design | DAM | 1 | DAM is implemented as a iterative process between an optimization phase and network analysis (powerflow and contingency analysis). For contingency analysis for CRR Offers, each distinct source/sink combination has to be analyzed separately. For example, the total number of CRR Offers submitted is 500. These 500 contain 100 distinct source/sink combinations. The number of contingencies to be analyzed is 2500. This leads to a total of 100*2500=250,000 powerflow executions. At present we expect the average number of iterations to be 7-8. To meet the DAM timeline we expect the network analysis to take 5 minutes for each iteration, optimization to take around 15 minutes at the most. We can meet the netowrk analysis timeline if the number of distinct source/sink combinations for CRR Offers are around 150 and the number of contingencies to be analyzed is 2500. If the number of distinct source/sink combinations exceeds this then network analysis timelines will dramatically deteriorate. | ? | Active
29 | ERCOT identifies self serve load and marks them in the CIM |  |  |  | ERCOT | Modeling? | DAM/RUC | 1 |  | John Adams/Ken Ragsdale | Active
30 | Congestion on Applied Energy (APD_ST1) | S_2073 APD_ST1 APD 138 APD 4.2 (08/05/10) | 21 | 2010-08-05 | ERCOT | Modeling/LDF Error | DAM/RUC | 1 | Severe congestion that is negatively impacting Houston Load Zone (HLZ) to Houston Hub spreads. DAM OD: 8/4/2010: Investigate non-adapting loads APD_APD_ST1 and APD_APD_AT1 which triggered very high shadow prices up to 50,000 $/MWH in DAM OD 8/4 A battery at station APD (Applied?) was introduced in DSV21 wih a LDF=80 MW that caused overloads with high shadow price and resulted in LZ_HOUSTON price to go upto $500. | sai | Model Updates |  | [ERCOT 8/5/2010] In DSV 21 additional changes were introduced in the network mdoel for APD. Further analysis and discussions with RE (submitting RARF for APD) has show that normal status of breakers were incorrect, LDF of one load APD_ST1 should be zero. This is in addition to rating change of line from deepwater to Applied that should be already in effect. With the normal status change (to OPEN) the contingency that is defined in DSV21 should be removed. [LUME 8/12/10] this constraint has occurred on 2 separate occasions between 8/4/10 and 8/5/10 and is typically associated with extremely high shadow prices (e.g. >$200,000). When this constraint is active, Houston Load Zone blows out over Houston Hub. A comment was made by ERCOT staff on the 8/5/10 conf. call that this is a step up xfmr that should be 'unchecked' for monitoring. Has this database change been made? [ERCOT 8/11/2010] ERCOT has changed this to a Non Conform Load and updated the load schedule. This change was submitted as part of the latest RARF update to the station which will be energized on 8/16 and will be in DSV23 (Scheduled NPROD date of 9/1/2010).
31 | DAM OD 8/4/2010: Generic constraint for import into DFW is incorrect in DSV 21 |  |  |  | ERCOT | Modeling/Software bug | DAM/RUC/EMS | 1 | The incorrect definition of generic constraint for import into the DFW area uncovered a bug in the way generic constraints limits are checked in MMS. Fix is expected to come in with MMS 5 P9 patch - ETA into NPROD - beginning of septmeber. This caused delay in DAM execution for OD 8/4/2010 | sai | Model Updates |  | Fix required for modeling error of generic constraint. [ERCOT 8/11/2010] Correction is expected to become effective in DSV23 (Scheduled NPROD date of 9/1/2010).
32 | LFC Test 8/4/2010 - double circuit contingecny 345KV sandow to temple caused overload of HEARNE Auto. | [6 empty] | 1 | Need 15 minute ratings data on HEARNE auto in order to implement RAP | John Adams | Active
33 | Wise County - Bridgeport 138 kV Line Rating | SBLSJAC8 560_A_1 WISECNTY 138 BRGPR 138 (08/10/10) | 22 | 2010-08-05 | LUME | Ratings Error | DAM | 1 | Congestion on this line seems to be negatively impacting Jack County | sai | Line Ratings Issue |  | [LUME 8/12/10] This line rating should be 388 MVA nominally (per NOMCR submitted by Brazos on 7/21/10) and was previously modeled as ~200 MVA. During the 5 Hour LFC test on 7/21/10 this rating was corrected by Brazos with a NOMCR and ERCOT loaded it into the EMS without delay. Some how, the old lower line rating started showing up in DAM again on 8/5/10 and has continued to show up nearly every DAM since then. This needs corrected ASAP to match the Brazos NOMCR. [ERCOT 8/12/2010] Per ONCOR: This a BEPC owned line that id jointly operated with Oncor. The ratings on this line were updated during the last 24 hour LFC test. This rating information is correct (388/388/388). It was lower at the start of the last 24 hour test. (DSV 22- Aug18) [LUME 8/16/10] When will the updated 388/388/388 MVA ratings make in back into Nodal production? As late as the DAM for 8/17/10, this line continues to constrain with a rating of ~188 MVA.
35 | Congestion on Navarro - Richland 69 kV Line | SAMGJEW8 2310__C NVARO 69 RCHLD 69 (08/10/10) | 21 | 2010-08-11 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting North Load Zone (NLZ) to North Hub spreads. | ? | Pending Closure - Radial Load Pockets | ? | [LUME 8/12/10] this constraint has occurred on 6 separate occasions between 7/27/10 and 8/11/10 and is typically associated with extremely high shadow prices (e.g. >$200,000). When this constraint is active, North Load Zone blows out over North Hub. [ERCOT 8/12/2010] DAM 08/05: Contingency SAMGJEW8 casuing overload from NVARO to RCHLD. Shadow price=97304 for HE 17.This contingency outages 1220_C and a bunch of lines (looks like multi sectional lines). Contingency causes a radial feed of loads from line between NVARO to RCHLD (69 KV 2310__C). Rating at hour 17 is 36 MW. It feeds the following radial loads - RCHLD_LD2101, COLDG_LDLXFMR2,COLDG_LDLXFMR1,WRTHM_LDLXFMR1,GRSMN_LDLXFMR1,MEXIA_LDLXFMR1,WTGLF_LDLOAD1
36 | Congestion on Kluge - Cyfair 138 kV Line | SSWCS8 CYFKL_76_1 KL 138 CYF 138 (08/10/10) | 21 | 2010-08-13 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Houston Load Zone (HLZ) to Houston Hub spreads. | ? | Pending Closure - Radial Load Pockets | ? | [LUME 8/12/10] this constraint has occurred on 2 separate occasions between 8/11/10 and 8/12/10 and is typically associated with very high shadow prices (e.g. >$16,000). When this constraint is active, Houston Load Zone blows out over Houston Hub. [ERCOT 8/12/2010]The line from Kluge to Cyfair is binding at its limit ( around 290MW) for peak hours under contingency SSWCS8: The shfit factor is only their to this constraint from LZ_HOUSTON and is around -2% Contingency SSWCS8 definition is to outage quite a few lines and breakers. In the post-contingency network, this line KL 138.0 CYF 138.0 becomes a radial line that feeds CYF_TR1, GE_TR1, GE_TR2, SA_TR7, and SA_TR8. So once again the energy only/PTP in LZ_HOUSTON is the only control variable with nozero shift factor for this constraint and the shift factor is simply sum of LDF of 5 loads. Correspondingly, LZ_HOUSTON is capped by this constraint and the shadow price on this constraint shot up.
37 | Congestion on ST. JO TU - SAINT JO 69 kV Line | BASE CASE | 21 | 2010-08-14 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting North Load Zone (NLZ) to North Hub spreads. | ? | Pending Closure - Radial Load Pockets | ? | [LUME 8/12/10] this constraint has occurred on 8 separate occasions between 6/11/10 and 8/12/10 (most recently on 8/11 and 8/12) and is typically associated with very high shadow prices (most recently on 8/12/10 >$516,000!). When this constraint is active, North Load Zone blows out over North Hub. [ERCOT 8/12/2010] This is a base case constraint from SNTJO to SAINT_JO. The line rating is 18MW. This line is a radial line that feeds four loads: These four loads are SAINT_JO_STJO___1, SAINT_JO_STJO___2, NOCONATN_NOCONA_2, and NOCONATN_NOCONA_1. The LDF are 1.031, 1.745, 4.088 and 3.510, respectively. Since it is a radial line in LZ_NORTH, only LZ_NORTH has shift factor -0.00079. Therefore, as well discussed before, LZ_NORTH is capped by this binding constraint and the line shadow price shot up. It seems that SAINT_JO_STJO___1 does not exist in current zonal production. However, its contribution is relatively small according to its LDF.
38 | Congestion on Garrett - Midtown 138 kV Line | DGBY_GS8 GT_MID90_1 GT 138 MID 138 (08/10/10) | 21 | 2010-08-15 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Houston Load Zone (HLZ) to Houston Hub spreads. | ? | Pending Closure | ? | [LUME 8/12/10] this constraint has occurred on 4 separate occasions between 8/5/10 and 8/12/10 and is typically associated with very high shadow prices (e.g. >$9,600). When this constraint is active, Houston Load Zone blows out over Houston Hub. [ERCOT 8/15/2010] DAM OD 08/11: At hour 12, its shadow price is 1400 $/MWh. This constraint is due to the contingency DGBY_GS8. It is a contnigency with outage elements from GBT to GABLE and from HARDY to CROKET. The rating in real time is via the telemetry and 311. However, the dynamic rating in DAM is 282 at hour 12. Assuming the given dynamic rating in DAM is correct, we have performed the sensitivity analysis and the dominant marginal resources are an Energy Only Bid at the Houston Load Zone whose shift factor is -0.002 and the generating units WAP_WAP_G1, WAP_WAP_G2, waP_WAP_G3 with shift factors of 0.04. [Dive mtg 8/17] - Confirmation of periodic real-time congestion, Wayne Kemper (Centerpoint) agreed to look at Garrett-to-Midtown since periodic in real-time, but chronic in DAM.
1 | Deepwater - Applied Energy 138 kV line rating |  | 23 | 2010-06-15 | LUME | Ratings Error | DAM | 2 | Is line rating correct? Shadow Price for the 138 kV line at its max was $13,149 (HE 16:00) and ave $6,618 for the Peak hours. The DAM Binding Shadow Price report indicates that line is rated at 48 MVA; however, the Summer 2010 SSWG case has the same line rated at 180/ 191/ 220 MVA (Normal/2 hr/15min MVA). | sai | Line Ratings Issue | Likely already resolved since this constraint hasn't bound since 7/17/10. | Please close the loop with summitter on whether this issue has been resolved [ERCOT 8/11/2010] ERCOT has contacted CNP about the rating on the line APDDW-2 coming out of the APD substation, and they have forwarded it the appropriate people in their company. A reply is expected by the end of the week. According to Centerpoint the 48 MVA rating on this line is correct and matches the SSWG case. I agree with Centerpoint that it is more than likely the 1 MW battery that could be causing problems here. A RARF was submitted recently to change the breaker status and expected load values at this station and a NOMCR has been submitted to make these changes with an energization date of 8/16. Hopefully these changes should correct any issues
2 | West - North Dynamic Stability limit |  |  | 2010-06-16 | LUME | Ratings Error | DAM | 2 | The limits being reported in Real Time are 2 – 3 times higher than the limits being reported in the DAM binding reports. How is the West – North Dynamic stability limit being modeled in the DAM? | sai | Line Ratings Issue | 2010-08-02 | This has been manually corrected. The last model load has the lower rating, but it was manually overridden in MMS. Corrected in DSV21 (2,400) [LUME 8/10/10] what rating for the West - North Stability Limit does ERCOT plan to utilize in the DAM model?
34 | LFC test 8/4/2010: putnam phase shifting transformer issue | [6 empty] | 2 |  | John Adams | Active
3 | Austrop 345/138 kV Auto Overloads |  |  | 2010-06-11 | LUME | SPS | DAM | 3 | Austrop autos overloading for the contingency loss of the other Austrop 345/138 kV Auto. Is Austrop SPS is not adequate enough to protect the Auto’s? Is this SPS being modeled in the DAM solution? | sai | Pending Software Update | Perhaps this has already been resolved since this constraint hasn't bound since 7/1/10. | Please close the loop with summitter on whether this issue has been resolved [LUME 8/10/10] suggest moving to Priority 3 until we see what happens when the vendor SPS solution is uploaded. What date does ERCOT expect that to occur? [ERCOT 8/10/2010] Software fix being deliverd 8/16. NPROD migration begining of septmeber after testing.
4 | SPS ¦ Elkton - Athens 138 kV Overloads |  |  | 2010-06-11 | LUME | SPS | DAM | 3 | Elkton – Athens 138 kV line overloading for the contingency loss of Trinidad – Stryker Creek & Trinidad – Mt. Enterprise 345 kV double circuit in DAM results. Does this mean that the SPS is not adequate enough to protect the Elkton – Athens – Forest Grove 138 kV line? Is this SPS being modeled in the DAM Solution? | sai | Pending Software Update | ? | Initially ERCOT believed that the the trigger point for the Elkton SPS had not been modeled correctly in the DAM (157MVA vs. 114MVA) and that the issue was going to be corrected in the DSV20 load on 7/26/10; however, this issue remains even for DAM results up through 7/30/10 [ERCOT 8/6/2010] The reason why this showed up again is due to the second issue with SPS - software issue - fixed in MMS5 P9 - tested DAM OD 7/28 at vendor site and verfied that SPS triggering issue is fixed and there are two contingencies (previous names DENTSC5 and DTRSENT5) for which SPS is properluy triggered and no constraints are generated. [LUME 8/10/10] suggest moving to Priority 3 until we see what happens when the vendor SPS solution is uploaded. What date is that expected to occur? [ERCOT 8/10/2010] Software fix being deliverd 8/16. NPROD migration begining of septmeber after testing.
12 | Congestion on Derby - Pearsall 138 kV line |  |  | 2010-07-19 | LUME | Modeling | DAM | 3 | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/19/10 NATF presentation for more detail). Possible cause - phase shifters, missing 345 KV line - san miguel - rio lobo? | sai | Active - Monitoring | ? | Between 5/4 & 7/15, bound 11 days in Nodal and 1 days in Zonal. ERCOT researched this and found that it was an incorrect contingency definition (reported at 7/29 NATF mtg). Issue still shows up in 7/31/10 DAM. When will Network model get corrected? [ERCOT 8/6/2010] As per ERCOT analysis presented at NATF- bad contingency definition SBATPEA8. Additionally, analysis presented during the 8/5/10 Nodal DAM Deep Dive, indicates that remaining overloads are due to Rayburn generation not participating in the DAM [LUME 8/10/10] suggest moving to a priority 2 until we see some DAM results that includes virtual offers that LUME intends to submit to make up for the generation that is apparently not particiating in the market trials in this area. [LUME 8/12/10] suggest moving to a priority 3 based on initial results of 8/11 and 8/12 DAMs where LUME submitted virtual offers to make up for missing generation in the Valley that effects this constraint. If this behaves well over the next several DAMs, then we should look at closing it out.
13 | Congestion on Pearsall 138/69 kV auto |  |  | 2010-07-19 | LUME | Modeling | DAM | 3 | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/19/10 NATF presentation for more detail). Possible cause - phase shifters, missing 345 KV line - san miguel - rio lobo? | sai | Active - Monitoring | ? | `[ERCOT 8/6/2010] Analysis presented during the 8/5/10 Nodal DAM Deep Dive, indicates that remaining overloads are due to Rayburn generation not participating in the DAM [LUME 8/10/10] suggest moving to a priority 2 until we see some DAM results that includes virtual offers that LUME intends to submit to make up for the generation that is apparently not particiating in the market trials in this area. [LUME 8/12/10] suggest moving to a priority 3 based on initial results of 8/11 and 8/12 DAMs where LUME submitted virtual offers to make up for missing generation in the Valley that effects this constraint. If this behaves well over the next several DAMs, then we should look at closing it out.
17 | Congestion on LaPalma - Villa Cavazos 138 kV line |  |  | 2010-07-29 | LUME | Modeling | DAM | 3 | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/29/10 NATF presentation for more detail) | sai/John Adams | Active - Monitoring | ? | [ERCOT 8/5/2010] Resources at SilasRay did not participate DAM. However, they were dispatched in Zonal real time. When SilasRay were not availble, DAM will reduce the generation from Duke, North Edinburg and curtail the clearing at LZ_SOUTH. 8/5/2010 John to ask PUB to participate in the DAM [ERCOT 8/12/2010]The most effective unit for solving this contingency constraint is: 'SILASRAY_SILAS_10' 'SILASRAY_SILAS_5' 'SILASRAY_SILAS_6' 'SILASRAY_SILAS_9' SILASRAY_SILAS_9 and SILASRAY_SILAS_6 consist of CC plant SILASRAY_CC1: SILASRAY_CC1_1 SILASRAY_SILAS_9 Primary CT SILASRAY_CC1_2 SILASRAY_SILAS_9 Primary CT SILASRAY_CC1_2 SILASRAY_SILAS_6 Primary ST All these four units have around -0.5 shfit factor. The sum of their HSL is about 100MW. However, none of them ( either regular unit and CC plant) participate in the 07/28 DAM MT ( no 3part offer at any hour). Without them, only CC units Duke, Frontera, and NE Edinbuurg have shift factor ( 0.0016, 0025843, 0.0015636 ) for this constraint. The LZ_SOUTH has around -0.04 shift factor for this constraint. Essentially, the units produced counter flow to balance the flow from LZ_SOUTH on this constraint. Since the unit shfit factor is much smaller, the LZ_SOUTH has to be curtailed to satisfy the constraint.
18 | Congestion on North Carbide - Port Lavaca 69 kV line |  |  | 2010-07-29 | LUME | Modeling | DAM | 3 | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/29/10 NATF presentation for more detail) | ? | Active - Monitoring | ? | [ERCOT 8/5/2010] This constraint does not contribute significantly to the SPP difference between south Load zone and south hub.This is a binding constraint due to contingency SLOLBLE8 . The contigency defition of SLOBLBE8 is to outage the line BLESSI_LOLITA1_1 from LOLITA to BLESSING. The binding constraint is at the line from NCARBIDE to PV_TAP at its limit of 61MW. At hour 17, its base case flow is 48MW. The base case flow of the outaged line from LOLITA to BLESSING is 152MW at hour 17. The key driver of this post-contingency flow include a number of large CC unit such as VICTORIA, LGE, INGLCO, NUE, CCEC, DUKE, etc, and a number of large PTP sources at these CC unit settlement points. The only resources that have effective negative shift factors are the small unit RAYBURN G1, G2, and G3 ( the shift factor is -0.048). Their HSL total is around 50MW. However, G1 and G2 are AS only and G3 is disconnected. With the binding constraint with expensive shadow price, such settlement point with positive shfit factor as FORMOSA and LGE have lower LMP and such settlement point with negative shfit factor such as RAYBURN and STP have higher LMP.
27 | NOIE CRR Offers restricted only to PCRRs? |  |  |  | ERCOT |  | DAM |  | There is a need to confirm whether a NOIE can submit a CRR Offer against ANY CRR Option they own into the DAM | ? | Active |  | [ERCOT 8/12/10] Mereness- MMS system enforces NOIE CRRs to be less than 120% Load
New | PSSe File Request | [9 empty] | Active |  | [ERCOT 8/12/2010]: Delivered for 8/4/2010 - 20 CDs delivered to 20 companies - Tools identified to reduce effort (but is still manual, not for post-go-live, and will be mailed or hand-delivered) - ERCOT targeting to release PSSe with subsequent model loads in Aug/Sept - PSSe file request for DSV 23/Sept 1 model Load to be created and sent via mail to 21 companies.
New | DAM 08/05: Contingency SSIGSAN8 causing overload from KenedySW to Kenedy - 69 KV (KENEDS_KENEDY1_1) for all 24 hours. Highest shadow price of $27000 set for hour 14. |  | 21 |  | ERCOT |  | DAM |  | [ERCOT 8/10/2010] This contingency outages 138 KV line from SANMIGL to SIGMOR. The overloaded line at 69 KV from kenedysw to kenedy is rated at 38 MW. The high shadow price at HE 14 is due to marginal CRR offers from CALAVERs to LZ_CPS. The shift factor difference between LZ_CPS and CALAVERS is positive and DAM buys back capacity. |  | Pending Closure |  | [ERCOT 8/10/2010] This contingency outages 138 KV line from SANMIGL to SIGMOR. The overloaded line at 69 KV from kenedysw to kenedy is rated at 38 MW. The high shadow price at HE 14 is due to marginal CRR offers from CALAVERs to LZ_CPS. The shift factor difference between LZ_CPS and CALAVERS is positive and DAM buys back capacity.
41 | Potential wrong line rating on Long Creek - Abilene Mulberry Creek 345 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous | ? | Line Ratings Issue | ? | [LUME 8/13/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
42 | Potential wrong line rating on Cleburne - Air Liquid 138 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line beween the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuos = | ? | Line Ratings Issue | ? | [LUME 8/13/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
43 | Potential wrong line rating on Big Spring - Airpark 138 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line beween the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuos = | ? | Line Ratings Issue | ? | [LUME 8/13/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
44 | Potential wrong line rating on Buda - Rutherford 138 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line beween the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuos = | ? | Line Ratings Issue | ? | [LUME 8/13/10] This line belongs to LCRA. LUME sent an email to Sergio Garza at LCRA to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
45 | Potential wrong line rating on Cedar Creek - Cedar Creek PU 138 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line beween the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuos = | ? | Line Ratings Issue | ? | [LUME 8/13/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
New | Stress Test update | [11 empty] | Stress test scenario to be copied into nProd for Aug 21 to allow market observation. More work being done to consider study of: - DAM solution where monitored, but not secured at the 69kv line level - DAM solution with tool from vendor to unsecure radial loads that can't be solved by generation
DSV22= Aug 18
DSV 23 = Sep 1
DSV24 = Sep 15

## Contingency Issues
Status | Contingency | DAM Issue # | Issue Description | Comments | Temporarily disabled/fixed in EMS | Temporarily disabled/fixed in MMS | Temporary fix verified 'as of' date * | Target DSV Resolved | Action Items
Pending DSV23 | DFORFRN5 | 22 | Invalid contingency; need NOMCR to remove from NMMS | Planning submitted a NOMCR: In-service date 8/14/10 | Yes | Yes | 2010-08-13 | Not fixed in DSV22, Will be fixed in DSV23 | Production support to disable after DSV22 load
Pending DSV23 | DELKMLS5 | 22 | Bad contingency definition; need NOMCR to remove from NMMS | A new contingency has been created to replace DTRCELK5; Planning submitted a NOMCR: In-service date 8/14/10 | Yes | Yes | 2010-08-13 | Not fixed in DSV22, Will be fixed in DSV23 | Production support to disable after DSV22 load
Resolved | DTRCELK5 | 22 | New contingency created to replace DELKMLS5; need to add in NMMS | New contingency to replace DTRCELK5; Planning submitted a NOMCR: In-service date 8/14/10 | NA | NA | 2010-08-13 | No fix required, already in DSV 21 | Production support to verify contingency
Pending DSV22 | SSD5SDS8 | 19 | Invalid contingency; ZBR versus a real line; need NOMCR to correct in NMMS | Planning submitted a NOMCR: In-service date 9/1/10 to correct in Model | Yes | Yes | 2010-08-13 | Fixed in DSV22 | Production support to verify after DSV22 load
Pending DSV22 | SPB5PBS8 | 19 | Invalid contingency; zBR versus a real line; need NOMCR to correct in NMMS | Planning submitted a NOMCR effective 9/1/10 to correct Model | Yes | Yes | 2010-08-13 | Fixed in DSV22 | Production support to verify after DSV22 load
No Contingency Issue | S_2073 | 30 | Valid contingency; creates a secondary island | Planning team waiting on Market Operations & Production Support to recommend next steps | NA | NA | 2010-08-13 | No fix required
Need to identify DSV number | SAMGJEW8 | 35 | Single Circuit, requires special modeling in NMMS to include additional definition elements | Planning submitted a NOMCR: In-service date 8/14/10 to include opening of autotransformer as part of the definition. | To be re-defined | Yes | 2010-08-13 | Network Modeling to confirm DSV# | Network Modeling to verify DSV# Grid Apps team to re-define in EMS Production support to disable in MMS
Need to Identify DSV number | SSD5SND8 | N/A | Invalid contingency; zBR versus a real line; need NOMCR to correct in NMMS | Planning submitted a NOMCR: In-service date 9/1/10 to correct Model | Yes | Yes | 2010-08-13 | It is not fixed in DSV22, may be in DSV23 | Production support to disable after DSV22 load
No Contingency Issue | SSWCS8 | 36 | high shadow prices in DAM because of this contingency creating a radial feed into a load pocket | Planning reviewed and believes the contingency is correctly defined | No | No | 2010-08-13 | No fix required
TBD | SBATPEA8 | 12 | Bad contingency definition presented at NATF | [5 empty] | Market Operations to research
* Note: Statuses confirmed by DA Operator & IT Support on 8/13/2010

## Line Rating Issues
Status | DAM Issue # | Line | Issue Description | Comments | Temporarily fixed in EMS | Temporarily fixed in MMS | Temporary fix verified 'as of' date * | Target DSV Resolved | Action Items
Temporary Fix in Place Pending Model Load | 6 | Hutto - Round Rock NE 138 kV | DAM line bound hourly Ratings Error, need to update Model | Line rating of 237, needs to be updated to 326 MVA normal rating. NOMCR submitted w/ Ratings 326/326/368 | Yes | Yes | 2010-08-12 | NOMCR submitted Corrected in DSV22 | Production Support to verify after DSV22 load
Pending Model Load | 20 | Bennett Rd. - Decartur Tap 138 kV | DAM congestion negatively impacting solution Ratings Error, NOMCR submitted 7/29/10 | Line rating of 124, needs to be updated to 186 MVA. NOMCR submitted 7/29 w/ Ratings 214/214/229. | No | No | 2010-08-17 | Corrected in DSV22 | Production Support to verify after DSV22 load
Pending Model Load | 21 | Decartur Tap - Rhome 138 kV | DAM congestion negatively impacting solution Ratings Error, need to update Model | Line rating of 124, needs to be updated to 186 MVA. Pending NOMCR submission | No | No | 2010-08-17 | NOMCR submitted by ONCOR, corrected in DSV23 | Network Modeling to send NOMCR to Operations planning to verify
Pending Model Load | 33 | Wise County - Bridgeport 138 kV | DAM congestion negatively impacting solution Ratings Error, need to update Model | Line rating of ~200, needs to be updated to 388 MVA. Brazos submitted NOMCR 7/21 | No | No |  | Brazos submitted NOMCR 7/21, corrected in DSV23 | Network Modeling to send NOMCR to Operations planning to verify
Pending NOMCR | 1 | Deepwater - Applied Energy 138kV | DAM Binding Shadow Price Report Ratings Error, need to update Model | Line rating of 48 MVA, may need to be updated to match SSWG case 180/191/220 MVA (Normal/2 hr/ 15 min). |  |  |  | Pending feedback / NOMCR from CNP. | Planning to work with Grid Support to verify LDFs
Resolved | 2 | West - North Dynamic Stability Limit | RT Ratings 2-3X higher than DAM Binding reports Ratings Error, need to update Model | Line rating of ?? MVA, manually updated to 2400 MVA | NA | NA | 2010-08-17 | Corrected in DSV21
| 26 | Numerous line ratings inconsistent | Comparison List Various line ratings inconsistent
Pending feedback / NOMCR | 41 | Long Creek - Abilene Mulberry Creek 345kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR
Pending feedback / NOMCR | 42 | Cleburne - Air Liquid 138kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR
Pending feedback / NOMCR | 43 | Big Spring - Airpark 138kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR
Pending feedback / NOMCR | 44 | Buda - Rutherford 138kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to LCRA to research and correct with NOMCR
Pending feedback / NOMCR | 45 | Cedar Creek - Cedar Creek PU 138kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR

## Model Issue Tracking
Status | DAM Issue # | Issue Description | Comments | Target Model Resolved
| 15 | Congestion on Trinidad - Winkler 138 kV line Severe congestion that is negatively impacting North Load Zone (NLZ) to North Hub spreads | Change Load to be zero in RARF- issues still to discuss versus systemic (psuedo measurement for SE)
Pending Model Load | 30 | Congestion on Applied Energy (APD_ST1) Severe congestion that is negatively impacting Houston Load Zone (HLZ) to Houston Hub spreads. | Changed to Non Conform Load and updated the load schedule. Submitted as part of the latest RARF update to the station which will be energized on 8/16 and will be in DSV23 (Scheduled NPROD date of 9/1/2010). | DSV23
Pending Model Load | 31 | DAM OD 8/4/2010: Generic constraint for import into DFW is incorrect in DSV 21 | Correction is expected to become effective in DSV23 (Scheduled NPROD date of 9/1/2010). | DSV23

## Old_Rating_Issues
DAM Shadow Price (Binding Constraints) |  |  |  | OPS Branch Data |  | Planning SSWG
Date | CTG Long Name | Binding Constraint long Name | Average Constraint Limit | Rate B | Rate C | Rate B | Rate C
2010-06-02 | AUSTROP- DAFFIN & - DECKER 138KV | GILLELAND - MCNEIL LCRA 138 kV | 248 | 221 | 228 | 493 | 493
2010-06-15 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR1) | 120 | 160 | 200 | 240 | 240
2010-06-16 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR1) | 120 | 160 | 200 | 240 | 240
2010-06-17 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR1) | 120 | 160 | 200 | 240 | 240
2010-06-18 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR1) | 120 | 160 | 200 | 240 | 240
2010-06-19 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR1) | 120 | 160 | 200 | 240 | 240
2010-06-22 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR1) | 120 | 160 | 200 | 240 | 240
2010-06-18 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR2) | 120 | 160 | 200 | 240 | 240
2010-06-19 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR2) | 120 | 160 | 200 | 240 | 240
2010-06-16 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR3) | 129 | 172 | 215 | 240 | 240
2010-06-19 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR3) | 129 | 172 | 215 | 240 | 240
2010-06-02 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR4) | 69 | 92 | 115 | 240 | 240
2010-06-03 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR4) | 69 | 92 | 115 | 240 | 240
2010-06-08 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR4) | 69 | 92 | 115 | 240 | 240
2010-06-15 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR4) | 69 | 92 | 115 | 240 | 240
2010-06-16 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR4) | 69 | 92 | 115 | 240 | 240
2010-06-17 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR4) | 69 | 92 | 115 | 240 | 240
2010-06-18 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR4) | 69 | 92 | 115 | 240 | 240
2010-06-22 | BASE CASE | BOSQUE SWITCH Auto (BOSQUESW_FMR4) | 69 | 92 | 115 | 240 | 240
2010-05-05 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_C1) | 75 | 125 | 125 | 125 | 125
2010-05-07 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_C1) | 75 | 125 | 125 | 125 | 125
2010-05-12 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_C1) | 75 | 125 | 125 | 125 | 125
2010-05-19 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_C1) | 75 | 125 | 125 | 125 | 125
2010-05-04 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_C2) | 75 | 125 | 125 | 125 | 125
2010-05-05 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_C2) | 75 | 125 | 125 | 125 | 125
2010-05-07 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_C2) | 75 | 125 | 125 | 125 | 125
2010-05-05 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_FMR2) | 111 | 185 | 185 | 185 | 185
2010-05-07 | BASE CASE | BUFFALO GAP Auto (BUFF_GAP_FMR2) | 111 | 185 | 185 | 185 | 185
2010-05-05 | BASE CASE | CHANNEL ENERGY CTR Auto (CHE_SUT1) | 150 | 250 | 250 | 250 | 250
2010-06-08 | BASE CASE | CHANNEL ENERGY CTR Auto (CHE_SUT4) | 150 | 250 | 250 | 300 | 300
2010-06-10 | BASE CASE | CHANNEL ENERGY CTR Auto (CHE_SUT4) | 150 | 250 | 250 | 300 | 300
2010-06-11 | BASE CASE | CHANNEL ENERGY CTR Auto (CHE_SUT4) | 150 | 250 | 250 | 300 | 300
2010-05-05 | BASE CASE | CORPUS CHRISTI ENERGY CTR Auto (CCEC_CTG1) | 135 | 225 | 225 | 248 | 248
2010-05-07 | BASE CASE | CORPUS CHRISTI ENERGY CTR Auto (CCEC_CTG1) | 135 | 225 | 225 | 248 | 248
2010-06-05 | BASE CASE | ENNIS CREEK SWITCH Auto (ECRSW_FMR1) | 24 | 28 | 42 | 28 | 28
2010-06-08 | BASE CASE | ENNIS CREEK SWITCH Auto (ECRSW_FMR1) | 24 | 28 | 42 | 28 | 28
2010-06-10 | BASE CASE | ENNIS CREEK SWITCH Auto (ECRSW_FMR1) | 24 | 28 | 42 | 28 | 28
2010-06-15 | BASE CASE | ENNIS CREEK SWITCH Auto (ECRSW_FMR1) | 24 | 28 | 42 | 28 | 28
2010-06-16 | BASE CASE | ENNIS CREEK SWITCH Auto (ECRSW_FMR1) | 24 | 28 | 42 | 28 | 28
2010-06-17 | BASE CASE | ENNIS CREEK SWITCH Auto (ECRSW_FMR1) | 24 | 28 | 42 | 28 | 28
2010-06-18 | BASE CASE | ENNIS CREEK SWITCH Auto (ECRSW_FMR1) | 24 | 28 | 42 | 28 | 28
2010-06-19 | BASE CASE | ENNIS CREEK SWITCH Auto (ECRSW_FMR1) | 24 | 28 | 42 | 28 | 28
2010-06-04 | BASE CASE | HOLLY POWER PLANT - BRACKENRIDGE 69 kV | 110 | 120 | 120 | 120 | 120
2010-05-20 | BASE CASE | LAREDO VFT Auto (LARDVFT_VFTN) | 115 | 127 | 127 | 127 | 127
2010-06-17 | BASE CASE | LAREDO VFT Auto (LARDVFT_VFTN) | 115 | 127 | 127 | 127 | 127
2010-06-18 | BASE CASE | LAREDO VFT Auto (LARDVFT_VFTN) | 115 | 127 | 127 | 127 | 127
2010-05-20 | BASE CASE | LAREDO VFT Auto (LARDVFT_VFTS) | 115 | 127 | 127 | 127 | 127
2010-06-17 | BASE CASE | LAREDO VFT Auto (LARDVFT_VFTS) | 115 | 127 | 127 | 127 | 127
2010-06-18 | BASE CASE | LAREDO VFT Auto (LARDVFT_VFTS) | 115 | 127 | 127 | 127 | 127
2010-05-07 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-12 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-19 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-20 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-21 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-25 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-26 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-27 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-28 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-06-02 | BASE CASE | LIMESTONE PLANT Auto (LEG_MT1) | 785 | 879 | 879 | 879 | 879
2010-05-04 | BASE CASE | LOBO - LAREDO VFT NORTH 138 kV | 224 | 861 | 861 | 861 | 861
2010-05-07 | BASE CASE | LOBO - LAREDO VFT NORTH 138 kV | 235 | 861 | 861 | 861 | 861
2010-05-19 | BASE CASE | LOBO - LAREDO VFT NORTH 138 kV | 211 | 861 | 861 | 861 | 861
2010-05-20 | BASE CASE | PASGEN Auto (PSG_XT2) | 150 | 230 | 250 | 250 | 250
2010-05-21 | BASE CASE | PASGEN Auto (PSG_XT2) | 150 | 230 | 250 | 250 | 250
2010-05-25 | BASE CASE | PASGEN Auto (PSG_XT2) | 150 | 230 | 250 | 250 | 250
2010-05-26 | BASE CASE | PASGEN Auto (PSG_XT2) | 150 | 230 | 250 | 250 | 250
2010-05-27 | BASE CASE | PASGEN Auto (PSG_XT2) | 150 | 230 | 250 | 250 | 250
2010-05-28 | BASE CASE | PASGEN Auto (PSG_XT2) | 150 | 230 | 250 | 250 | 250
2010-06-02 | BASE CASE | PASGEN Auto (PSG_XT2) | 150 | 230 | 250 | 250 | 250
2010-05-20 | BASE CASE | PASGEN Auto (PSG_XT3) | 150 | 230 | 250 | 250 | 250
2010-05-21 | BASE CASE | PASGEN Auto (PSG_XT3) | 150 | 230 | 250 | 250 | 250
2010-05-25 | BASE CASE | PASGEN Auto (PSG_XT3) | 150 | 230 | 250 | 250 | 250
2010-05-26 | BASE CASE | PASGEN Auto (PSG_XT3) | 150 | 230 | 250 | 250 | 250
2010-05-27 | BASE CASE | PASGEN Auto (PSG_XT3) | 150 | 230 | 250 | 250 | 250
2010-05-28 | BASE CASE | PASGEN Auto (PSG_XT3) | 150 | 230 | 250 | 250 | 250
2010-06-02 | BASE CASE | PASGEN Auto (PSG_XT3) | 150 | 230 | 250 | 250 | 250
2010-05-07 | BASE CASE | POWER SYSTEMS-ARCO COGEN Auto (PSA_TR1) | 90 | 168 | 168 | 168 | 168
2010-05-04 | BASE CASE | ROANOKE SWITCH - ELIZABETH CREEK 138 kV | 176 | 237 | 237 | 237 | 237
2010-06-23 | BASE CASE | SILVER CITY - BARCLAY 69 kV | 19 | 36 | 36 | 36 | 36
2010-05-07 | BASE CASE | SWEETWATER WIND 4 / SWEETWATER GEN 5 Auto (SWEETWN4_5) | 90 | 99 | 113 | 134 | 153
2010-05-07 | BASE CASE | WOLF HOLLOW GEN Auto (WHCCS_1HX) | 168 | 281 | 281 | 281 | 281
2010-05-19 | BASE CASE | WOLF HOLLOW GEN Auto (WHCCS_1HX) | 168 | 281 | 281 | 281 | 281
2010-05-20 | BASE CASE | WOLF HOLLOW GEN Auto (WHCCS_1HX) | 168 | 281 | 281 | 281 | 281
2010-05-21 | BASE CASE | WOLF HOLLOW GEN Auto (WHCCS_1HX) | 168 | 281 | 281 | 281 | 281
2010-05-04 | BAYTON ENERGY CTR - CHAMBERS 345KV | BAYTOWN ENERGY CTR Auto (BTE_AT-1) | 480 | 600 | 600 | 600 | 600
2010-05-07 | BAYTON ENERGY CTR - CHAMBERS 345KV | BAYTOWN ENERGY CTR Auto (BTE_AT-1) | 480 | 600 | 600 | 600 | 600
2010-05-04 | BAYTON ENERGY CTR - CHAMBERS 345KV | BAYTOWN ENERGY CTR Auto (BTE_AT-2) | 480 | 600 | 600 | 600 | 600
2010-05-07 | BAYTON ENERGY CTR - CHAMBERS 345KV | BAYTOWN ENERGY CTR Auto (BTE_AT-2) | 480 | 600 | 600 | 600 | 600
2010-05-05 | BAYTOWN EN.CTR AT1 345/138KV | BAYTOWN ENERGY CTR Auto (BTE_AT-2) | 480 | 600 | 600 | 600 | 600
2010-05-05 | BAYTOWN EN.CTR AT2 345/138KV | BAYTOWN ENERGY CTR Auto (BTE_AT-1) | 480 | 600 | 600 | 600 | 600
2010-06-04 | COLETO CREEK TO VICTORIA 138KV | COLETO CREEK - VICTORIA 138 kV | 303 | 303 | 303 | 320 | 320
2010-06-11 | COLETO CREEK TO VICTORIA 138KV | COLETO CREEK - VICTORIA 138 kV | 303 | 303 | 303 | 320 | 320
2010-05-07 | COMANCHE PEAK UNITS 1&2 345KV | SHARON RIDGE EXXON - BLUFF CREEK SWITCH 138 kV | 158 | 186 | 186 | 186 | 186
2010-05-04 | COMANCHE PEAK UNITS 1&2 345KV | WKN BREAKER - MEC PLAINVIEW TAP 69 kV | 63 | 74 | 74 | 74 | 74
2010-05-07 | COMANCHE PEAK UNITS 1&2 345KV | WKN BREAKER - MEC PLAINVIEW TAP 69 kV | 63 | 74 | 74 | 74 | 74
2010-05-12 | COMANCHE PEAK UNITS 1&2 345KV | WKN BREAKER - MEC PLAINVIEW TAP 69 kV | 63 | 74 | 74 | 74 | 74
2010-06-02 | ELGIN SW TO SANDOW SW 138KV | GILLELAND - MCNEIL LCRA 138 kV | 248 | 221 | 228 | 493 | 493
2010-05-04 | ELM CREEK TO SAN MIGUEL GEN 345KV | CALAVERS FACILITY - PAWNEE 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-06-04 | ELM CREEK TO SAN MIGUEL GEN 345KV | CALAVERS FACILITY - PAWNEE 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-06-22 | ELM CREEK TO SAN MIGUEL GEN 345KV | CALAVERS FACILITY - PAWNEE 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-06-23 | ELM CREEK TO SAN MIGUEL GEN 345KV | CALAVERS FACILITY - PAWNEE 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-05-07 | ELM CREEK TO SAN MIGUEL GEN 345KV | PAWNEE - CALAVERS FACILITY 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-05-12 | ELM CREEK TO SAN MIGUEL GEN 345KV | PAWNEE - CALAVERS FACILITY 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-05-21 | ELM CREEK TO SAN MIGUEL GEN 345KV | PAWNEE - CALAVERS FACILITY 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-05-28 | ELM CREEK TO SAN MIGUEL GEN 345KV | PAWNEE - CALAVERS FACILITY 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-06-05 | ELM CREEK TO SAN MIGUEL GEN 345KV | PAWNEE - CALAVERS FACILITY 345 kV | 717 | 1076 | 1076 | 1076 | 1076
2010-05-12 | FERGUSON TO WIRTZ 138KV | WIRTZ Auto (WIRTZ_GSU1) | 33 | 34 | 34 | 48 | 48
2010-05-20 | FERGUSON TO WIRTZ 138KV | WIRTZ Auto (WIRTZ_GSU1) | 33 | 34 | 34 | 48 | 48
2010-05-25 | FERGUSON TO WIRTZ 138KV | WIRTZ Auto (WIRTZ_GSU1) | 33 | 34 | 34 | 48 | 48
2010-05-26 | FERGUSON TO WIRTZ 138KV | WIRTZ Auto (WIRTZ_GSU1) | 33 | 34 | 34 | 48 | 48
2010-05-28 | FERGUSON TO WIRTZ 138KV | WIRTZ Auto (WIRTZ_GSU1) | 33 | 34 | 34 | 48 | 48
2010-06-18 | FERGUSON TO WIRTZ 138KV | WIRTZ Auto (WIRTZ_GSU1) | 33 | 34 | 34 | 48 | 48
2010-06-23 | FERGUSON TO WIRTZ 138KV | WIRTZ Auto (WIRTZ_GSU1) | 33 | 34 | 34 | 48 | 48
2010-05-20 | FORNEY SW-FORNEY FLORIDA P&L 345KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-21 | FORNEY SW-FORNEY FLORIDA P&L 345KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-06-19 | GRAHAM SES TO RICE SWITCH 138KV | ORAN TMPP - MORRIS SHEPPARD 69 kV | 25 | 23 | 23 | 194 | 194
2010-05-21 | HILLCTY TO MAR & TO ELMCRK 345KV | MARION - SKYLINE 345 kV | 956 | 1076 | 1076 | 1076 | 1076
2010-05-07 | JACK COUNTY TO RENO 138KV | WISE COUNTY - BRIDGEPORT TU 138 kV | 211 | 186 | 196 | 326 | 326
2010-05-12 | JACK COUNTY TO RENO 138KV | WISE COUNTY - BRIDGEPORT TU 138 kV | 207 | 186 | 196 | 326 | 326
2010-05-26 | JACK COUNTY TO RENO 138KV | WISE COUNTY - BRIDGEPORT TU 138 kV | 209 | 186 | 196 | 326 | 326
2010-05-28 | JACK COUNTY TO RENO 138KV | WISE COUNTY - BRIDGEPORT TU 138 kV | 199 | 186 | 196 | 326 | 326
2010-06-02 | JACK COUNTY TO RENO 138KV | WISE COUNTY - BRIDGEPORT TU 138 kV | 205 | 186 | 196 | 326 | 326
2010-05-04 | LAREDO VFT NORTH UNITS 4 & 5 138K | LOBO - LAREDO VFT NORTH 138 kV | 224 | 861 | 861 | 861 | 861
2010-05-25 | LIMESTONE PLANT UNIT LEG_G2 345KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-12 | LYTTON SPRING-ZORN & AUSTROP-ZORN | TURNERSVILLE - BUDA 138 kV | 287 | 287 | 287 | 439 | 439
2010-05-20 | LYTTON SPRING-ZORN & AUSTROP-ZORN | TURNERSVILLE - BUDA 138 kV | 287 | 287 | 287 | 439 | 439
2010-06-04 | LYTTON SPRING-ZORN & AUSTROP-ZORN | TURNERSVILLE - BUDA 138 kV | 287 | 287 | 287 | 439 | 439
2010-06-05 | LYTTON SPRING-ZORN & AUSTROP-ZORN | TURNERSVILLE - BUDA 138 kV | 287 | 287 | 287 | 439 | 439
2010-05-20 | MARION TO GUADALUPE GEN 345KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-21 | MARION TO GUADALUPE GEN 345KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-07 | MARION-HILL COUNTRY & SKYLINE 345 | ELM CREEK - HILL COUNTRY 345 kV | 430 | 1076 | 1076 | 1076 | 1076
2010-05-19 | MARION-HILL COUNTRY & SKYLINE 345 | ELM CREEK - HILL COUNTRY 345 kV | 430 | 1076 | 1076 | 1076 | 1076
2010-05-28 | MARTIN LAKE - SCSES & - ENTERPRISE | ELKTON - FORNEY SWITCH 345 kV | 721 | 717 | 825 | 956 | 1072
2010-05-21 | MGSES-QALSW & - LNGSW 345KV | GARDEN CITY - CHALK 69 kV | 24 | 24 | 27 | 42 | 42
2010-05-26 | MGSES-QALSW & - LNGSW 345KV | GARDEN CITY - CHALK 69 kV | 24 | 24 | 27 | 42 | 42
2010-06-04 | MGSES-QALSW & - LNGSW 345KV | GARDEN CITY - CHALK 69 kV | 24 | 24 | 27 | 42 | 42
2010-05-04 | ROMA SW TO FALCON SW ST 13KV | LOBO - LAREDO VFT NORTH 138 kV | 224 | 861 | 861 | 861 | 861
2010-05-07 | ROMA SW TO FALCON SW ST 13KV | LOBO - LAREDO VFT NORTH 138 kV | 235 | 861 | 861 | 861 | 861
2010-05-12 | ROMA SW TO FALCON SW ST 13KV | LOBO - LAREDO VFT NORTH 138 kV | 239 | 861 | 861 | 861 | 861
2010-05-20 | ROUND ROCK TO HUTTO 138KV | GILLELAND - MCNEIL LCRA 138 kV | 253 | 221 | 228 | 493 | 493
2010-05-28 | ROUND ROCK TO HUTTO 138KV | GILLELAND - MCNEIL LCRA 138 kV | 255 | 221 | 228 | 493 | 493
2010-05-20 | SANDOW SES TO TAYLOR 138KV | ELGIN SWITCH - GILLELAND 138 kV | 220 | 220 | 220 | 508 | 508
2010-05-21 | SANDOW SES TO TAYLOR 138KV | ELGIN SWITCH - GILLELAND 138 kV | 220 | 220 | 220 | 508 | 508
2010-05-07 | SKYLINE TO MARION & ELMCREEK 345KV | ELM CREEK - HILL COUNTRY 345 kV | 430 | 1076 | 1076 | 1076 | 1076
2010-05-12 | SPRING TO WOLFRIDGE 138KV 138KV | KRUM - KRUM TAP 138 kV | 96 | 84 | 85 | 214 | 214
2010-06-02 | TRINIDAD SES-RICHLAND CHAMBERS 345 | BIG BROWN SES - VENUS SWITCH 345 kV | 956 | 956 | 1100 | 1072 | 1072
2010-05-20 | WA PARISH UNITS 5 & 6 138KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-21 | WA PARISH UNITS 5 & 6 138KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-25 | WA PARISH UNITS 5 & 6 138KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-20 | WA PARISH UNITS 6 & 8 345KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-21 | WA PARISH UNITS 6 & 8 345KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-25 | WA PARISH UNITS 6 & 8 345KV | BUFFALO GAP Auto (BUFF_GAP_C1) | 100 | 125 | 125 | 125 | 125
2010-05-04 | WILLOW VALLEY SW TO BLUFF CR 138KV | KEY - LAMESA 138 kV | 161 | 143 | 165 | 186 | 186
2010-06-19 | WINK TAP TO WINK 138KV | PERMIAN BASIN SES - WICKETT TNP 69 kV | 60 | 60 | 82 | 80 | 95

## Closed
Issue # | Issue Title | Date Submitted | Submitter | Category | Mkt. | Priority | Issue Description | Assigned To | Status | Estimated Resolution Date | Comments
7 | Contingency Definition Report | 2010-08-02 | LUME | Reports | DAM | 1 | The Contingency Definition Report Provided on 8/1/2010 by Alan Adams, doesn't contain all the contingency names. Problems with DSV20, DSV21 | John Adams | Closed | ? | Additionally, it needs to contain the contingency definitions (i.e. what branches are outaged) for each of the contingency defintions. 8/5/2010 - new report for DSV 20 and DSV 21 will be created by NMMS. Need to figure out how this will be posted. The contingency names will be consistent from DSV 22 ONWARDS [LUME 8/12/10] - this issue was closed at the 8/10/10 conf. call, as all the necessary reports for DSV 20 and 21 had been delivered on 8/6/10. Thanks!
23 | Congestion on S.E. Nacogdoches 345/138 kV auto | 2010-07-29 | LUME | Modeling | DAM | 3 | Congestion on this auto appears to be legitimate (see 7/29/10 NATF presentation for more detail) | ? | Closed | ? | This congestion should be elimiated soon by SPS #21 that Oncor is installing during the Fall of 2010 [LUME 8/10/10] Suggest moving to Priority 3 and monitor the impact of the upcoming SPS #21 installation [LUME 8/12/10] Suggest moving to Closed status given that Oncor will be installing SPS #21 in the Fall of 2010

## SAMPLE-DAM Report
DELIVERYDATE | HOURENDING | STL_PNT | TOTAL_DAM_ENERGY_BOUGHT | TOTAL_DAM_ENERGY_SOLD | TOTAL_PTP_OBL_AWARDED_SOURCE | TOTAL_PTP_OBL_AWARDED_SINK | TOTAL_CRR_NONDAMAWARDED_SOURCE | TOTAL_CRR_NONDAMAWARDED_SINK
2010-08-13 | 1 | HB_HOUSTON | 120 |  | 73.9 | 346 |  | 92.5
2010-08-13 | 1 | HB_HUBAVG | 1 |  | 122.9 | 270.3
2010-08-13 | 1 | HB_NORTH | 1546.4 |  | 37.3 | 357.2 |  | 226.4
2010-08-13 | 1 | HB_SOUTH | 326 | 2 |  | 306.7 |  | 232.7
2010-08-13 | 1 | HB_WEST | 365.2 | 20 | 63.3 | 97.8
2010-08-13 | 1 | LZ_HOUSTON | 1321 | 10.3 | 61.1 | 1074.8
2010-08-13 | 1 | LZ_NORTH | 2993 | 28.5 | 32.3 | 2169.9
2010-08-13 | 1 | LZ_SOUTH | 1166 |  |  | 1689.9
2010-08-13 | 1 | LZ_WEST | 935.1 | 2 | 31.1 | 107.6