Updated 8/26/2010

| TSP Combined Issues List 7/7/20-NDSWG agreement)10 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Number | Priority | Issue Description | Impact to Transmission Operations | Potential Resolution | Comments |  |  |  |  |
| NMMS Business Process Issues |  |  |  |  |  |  |  |  |  |
| 1 – ME Paper | 2 | What is the definite on of an Interim Update? The protocols give ERCOT 15 days to review the NOMCR for completeness. Responding to ERCOT’s request during this review period does not cause the NOMCR to convert to an Interim Update. Design of the Interim Update approval process and how interim updates have not yet been vetted in the NDSWG | The submittal of interims updates are allowed by the protocols. However the protocols don't clearly defined what type of changes to the ERCOT network model can be made as an interim updates | The Protocols need to clearly state that all types of changes to the network model will be accept as an interim update with the understanding that these change will be implemented with the full review of the IMM. | 7/20-NDSWG agreement) The ME whitepaper has established a framework to define this term. NDSWG will be the forum for future Interim Update discussions including possible workshops on the issue. MPs in NDSWG will consider a NPPR to define the term Interim Update in Protocols post go-live. 7/20-NDSWG agreement) MPs agree to go forward with the principles in the ME paper and the August training with the caveat that it can be modified, to maximize operational efficiency or adjust to Protocol changes. 7/20-NDSWG agreement) This condition is defined in the ME paper and is not considered as an Interim Update - 7/26-Workshop ) MPs want further review of the ME paper - 7/26-Workshop ) NDSWG should review Interim Update implementation and definition on a quarterly basis after go-live. - MPs want further review of the ME v3.0 paper; comments are due on 8/4/2010 |  |  |  |  |
| 2 – potentially resolved | 2 | Processes for operational status changes need to be addressed before go-live. | There are many types of operational changes that are performed in the real-time that need to be reflected into the NMMS application. Most of these changes are not controlled by the ERCOT protocols. Examples are operational changes to switching status (what lines are being operated normally open), what voltage is being regulated to by generators, autotransformers or capacitors, what are the operating taps on an autotransformer. | Operational changes that occur in the real-time, as such should not be treated as an interim update. The ERCOT protocols should be updated to reflect this and allow these changes so that the NMMS network model provides the must accurate information possible about the transmission system. | There is perception that there are not protocol changes being driven because of metric issues. 7/20-NDSWG agreement) MPs agree to use existing tools to manage operational changes. MPs will review operational efficiency after Go-live to decide if NPRRs are necessary to exclude some model changes as Interim Updates. Additional outage types or modification to existing outage types may also be necessary post go-live. 7/26-Workshop ) MPs expressed some concern about using the OS for making changes in the longer term (3 month time period). Concern could be resolved through system changes or through Metric category revisions. 8-18-10 Nodal Engagement Call) Waiting on feedback from Oncor 8-25-10 Nodal Engagement Call) ERCOT will investigate FOD issues for CAP banks. |  |  |  |  |
| 3 – monitor | High 2 | System Performance issues with NMMS needs to be resolved. | The performance of the NMMS application has been substantially degraded since the last major update of the application. It takes more then 10 minutes to validate changes to the model. There are times when you might be disconnected from the server due to this delay. When you restart the IMM session there is a possibility that the model change will need to be re-entered into NMMS. This could be the lost of hours of work. Do to timing issues when submitting these changes what might have been a standard time NOMCR submission might become an Interim update. | The performance of the NMMS application needs to be improved so that the system does not disconnect the users. This leads to loss of submitted data. A long validation time, sometimes in excess of 30 minutes, leads to user frustration and loss of continuity when submitting changes. ERCOT has indicated that they have Siemens working on this issue | This could have further impact to the market if changes cannot be submitted in a timely manner and the energization date must be delayed for one month. This has been an issue since May 1. ERCOT/ Siemens need to get this resolved. We are scheduled to begin following nodal protocol timelines August 1, and we cannot have this issue unresolved by then. 7/20-NDSWG agreement) MPs agree this item could become a Priority 1 if performance does not improve. Freezing of the UI is a major concern along with navigation times and validation times. This is an open item to be monitored and discussed at future NDSWG meetings. 7/20-NDSWG agreement) MPs would like to be able to discuss items directly with Siemens in a face-to-face meeting. ERCOT has declined this request. 7-26 ERCOT) New patches have added to the stability and performance of the system. Navigation has gotten better, but validation still needs to be addressed. |  |  |  |  |
| 4 – ME paper | 2 | What is the process for placing NOMCRs into service under Nodal protocols? | In the Zonal process ERCOT has a document call 'Transmission and Generation Energize Approval' This process has not been defined for the Nodal process. | ERCOT needs to update this process document to follow Nodal requirements. | Need prior to the 168 Hour Test. 7/20-NDSWG agreement) The ME paper will include A2E process prior to the August training. The Nodal A2E procedure will be provided to MPs. |  |  |  |  |
| Documentation Needs |  |  |  |  |  |  |  |  |  |
| 5 – ME paper | 2 | Network Operations Modeling Expectations needs to have a clear description of how the Network Model and the Outage Scheduler systems are to work together on issues such as 1) how new equipment is to be energized and loaded into the outage scheduler (i.e. an operating procedure would be good); 2) how retiring equipment is to be decommissioned in the Network Model and Outage Scheduler (i.e. an operating procedure would be good here too) | Clear procedures will allow consistency and reduce unnecessary errors | Develop procedures and operating guides for consistency among TSPs and less errors, few interim upgrades. | Network Operations Modeling Expectations needs to have a clear description of how the Network Model and the Outage Scheduler systems are to work together on issues such as 1) how new equipment is to be energized and loaded into the outage scheduler (i.e. an operating procedure would be good); 2) how retiring equipment is to be decommissioned in the Network Model and Outage Scheduler (i.e. an operating procedure would be good here too) 7/20-NDSWG agreement) MPs agree that this item is covered in the ME paper and in the August training. 7/26-Workshop ) MPs may want to ask for further details after reviewing MP3.0 |  |  |  |  |
| 6 – ME paper | 2 | What is the process for using Outage Scheduler for energizing new or relocated facilities? | ERCOT needs to provide MPs the process that should be used to notify ERCOT when placing new or relocated facilities into service. The protocols require that the ERCOT Outage Scheduler be used for this activity. The MPs have not been provided any training to accomplish this task | ERCOT needs to provide MPs the process that should be used to notify ERCOT when placing new or relocated facilities into service. The protocols require that the ERCOT Outage Scheduler be used for this activity. The MPs have not been provided any training to accomplish this task | It appears the software does not match the Protocols concerning relocation of existing lines. TSPs may not be able to use the Outage Scheduler to relocate an existing line to a new breaker on another buss. This may be due to the line will have the same name (under business practice) and if the breaker and line timing are off a day or two, there is no mechanism to take the line in Outage Scheduler to match the still energized old breaker. TSPs have no feedback from ERCOT on ICCP relinking verses Outage Scheduler to 7/26-Workshop ) The ME paper will include A2E process prior to the August training. The Nodal A2E procedure will be provided to MPs. |  |  |  |  |
| 7 – ME paper | 2 | Outage Scheduler is being use for much more than it was intended (Energization of new construction, retirement of old equipment, construction modifications …). The Documentation for the Outage Scheduler and schedule has not been shared with TSPs. AEP is unsure of the go-live plan and schedule as of 6/15/10 | This results in NMMS & Outage Scheduler needing to be highly coordinated. In the event there are minor discrepancies between these systems. Upgrades and network changes could be delayed and not reflect what is actually happening on the grid. | No proposed solution. Need to discuss with ERCOT. | 7/20-NDSWG agreement) ERCOT has supplied NATF with an OS cutover presentation. The plan is due at TAC next month. ERCOT will provide a cutover document that details the interactions necessary during the transition. 7/20-NDSWG agreement) The ME paper and August training address the coordination needed between MP Outage and Modeling groups. 7/26-Workshop ) MPs may have further questions once the documents are reviewed |  |  |  |  |
| 8 - potentially resolved | 3 | What is the ERCOT business for managing and approving SPSs? | When will ERCOT have the 'Procedure for Approval and Distribution of RAP MP and SPS ' documentation updated to reference Nodal Protocols? | Update the document to reference Nodal Protocols and process. | 7/20-NDSWG agreement) ERCOT will add documentation of the SPS approval process in the ME paper along with clarification about whether a RAP may be classified as a category 3 or 4 according to the need. 7/26-Workshop ) MPs may have further questions once the documents are reviewed |  |  |  |  |
| 9 - resolved | 2 | What does a November 1st Binding date mean for Outage Scheduler? | ERCOT when presenting the transition plan for the outage scheduler showed a binding date to the Nodal Protocols for the Outage Scheduler of November 1st. What does this mean? Outages in the Zonal Outage Scheduler are treated using the Zonal Protocols and the Nodal Outage Scheduler uses the Nodal Protocols? Or is there some combination? | Provide a business process that clarifies this transitional period. | 7/20-NDSWG agreement) The OS cutover plan will detail why the November 1 deadline is binding. ERCOT will consult with Legal about when the Zonal and Nodal protocols are applicable to MPs. 7/23 ERCOT comments) The Cutover Handbook that includes the OS cutover. My desire is to turn on the Nodal time line starting with the 90 day and 45 day submission timeline Nov 1 that would allow MPs to submit Nodal outages in Nov for the month of Dec. We will turn on the 9 day timeline and the 3 and 4 day timeline before cut over during the month of November so that MPs will submit outages for go-live periods as a phased in process. I'll be working on a detailed plan so the MPs will only need to submit outages in the timelines to cover the go-live period. 8-18-10 Nodal Engagement Call) Waiting on feedback from Oncor 8-25-10 Nodal Engagement Call) MPs agree that this issue is closed. |  |  |  |  |
| Modeling Issues |  |  |  |  |  |  |  |  |  |
| 10 – ME paper | 3 | The role and amount of information expected from the TSP is more than expected and outside many of the protocols. | More resources and effort by the TSP resulting in higher costs than anticipated There are 3 potential impacts: 1. Date of energization for used and useful and the TSP can get paid for an energized asset on new facilities. 2. Customer Impact if a shift due to change in energization due to interim updates as well as the impact on revenue collection. 3. There are concerns that some one could come back and sue a TSP for an interim update which caused a market participant to lose money. The interim update has no impact on reliability; it is strictly for use by ERCOT. | Clarification of the TSP roles and a process for eliminating redundant information. Amnesty for providing interim updates. Would ERCOT consider allowing TSPs some number of interim updates and allow TSPs to prioritize and allow the interim updates to be implemented? | Interim Updates can impact reliability and that statement was removed. However, there are many changes that do not impact topology and really shouldn't be classified as an interim update. Interim updates can have impact on reliability and that statement probably needs to be removed. However, there are many, many changes that do not affect topology and really shouldn't be classified as interim updates. Also, all interim updates are at ERCOT discretion and there aren’t any rules on what will or will not be allowed. A great potential exists to have stranded assets for several weeks if ERCOT will not allow an interim update. ERCOT processes as described in their white paper are all built around the assumption that interim updates will practically never happen and I'm not sure that is a good assumption to build all of their processes around. 7/20-NDSWG agreement) ERCOT believes much of the uncertainty around interim updates was clarified by the ME paper and subsequent NDSWG discussions. Changes allowing “amnesty” or exclusion of certain NOMCRs from the interim update classification would require a Protocol change. 7/26-Workshop ) MPs expressed concern about some model elements were beyond expectations. MPs will provide details. |  |  |  |  |
| 11 - resolved | 2 | All CNP line names have an extra character (“1”) appended to the end of the line names. We understand this is necessary for some asset owners in ERCOT. This extra numerical character is a source of confusion to CenterPoint Energy users and systems and should be removed. Our users and our systems expect the same equipment names (including lines) in ERCOT’s NMMS system. For example, Line NEWTGF04 incorrectly appears as NEWTGF041 in the Nodal outage scheduler. Would you eliminate the extra characters appended to CenterPoint energy line name? We have crossed checked in NMMS and verified these extra character are not part of our line identifiers. (Applies to both Human Interface and web services interface) |  |  | Need by 168 Hour Test. 7/20-NDSWG agreement) ERCOT will work with affected TSPs to replace the “1” in the line segment place with a non-numeric character. This will resolve the Go-live problem. (CNP and AEP are the only identified TSP as of 7/20-NDSWG agreement)/10) As a related item, the line naming consistency in EMS/MMS/OS needs to be investigated as a result of this work-around. Line names may not be the exactly the same such as NEWTGF04_ in OS NEWTGF04 _ in ERCOT EMS (MMS) NEWTGF04 in MP OS ERCOT will take responsibility for this and report back to the NDSWG group to see if additional action is required. 7/23 ERCOT comments) A defect has been created and deferred for this issue for future tracking after go live. We are looking at the From station coming from EIP. 7/26-Workshop ) SCR759 needs to be considered in the ultimate resolution. 8/18/10 Nodal Engagement Call) CNP has submitted a NOMCR as a workaround for Go-live. Issue needs to be addressed after SCR 759 issue is resolved. |  |  |  |  |
| 12 – ME paper | 3 | ERCOT's current Modeling Expectations (non-binding document) puts modeling and outage scheduling burden on TSPs. | ERCOT is introducing confusion between equipment "energization" and "Model ready" dates. It also increases model submittal timelines for TSPs. Additionally, this may force potential use of pseudo equipment and expected maintenance burden. |  |  |  |  |  |  |
| 13 - potentially resolved | 2 | ERCOT introduced NOMCRs (associated with TSP owned equipment) should remain ERCOT responsibility from a compliance perspective. |  |  | 7/20-NDSWG agreement) If ERCOT requires MP to submit an interim update for ERCOT-required changes, ERCOT will assume responsible from a compliance perspective. 8/18/2010 – In the ERCOT comment field it will be noted that the change was made at ERCOT’s request and that it was requested after the 90-day timeline. |  |  |  |  |
| 14 – Gray box | 2 | Monthly Database Load: Requirement to have information for NMMS locked in on the 15th of the Month rather than a rolling schedule | ERCOT needs to provide a process where there is a two week lock down prior to each weekly database load. A potential exists that it may be up to six weeks to energize a piece of equipment if a NOMCR problem is discovered at the last minute. ERCOT needs to have some reasonable mechanisms to accommodate interim updates. | Reasonable interim update policy. Rolling two week lock down requirement prior to each database load. Access by TSPs to a forward looking test environment to verify NOMCR and telemetry prior to energization. | NDSWG has asked several times about access to an ERCOT test environment to validate models prior to them being put into production. In our own shops, we will typically load a new model on a development system to verify changes and telemetry prior to putting it into production. We would like a similar capability with ERCOT. If ERCOT is going to push the modeling responsibilities onto the TSPs and then lock down any ability to make last minute changes through interim updates, then the TSPs need better tools to evaluate NOMCR being put into production prior to production dates. 7/20-NDSWG agreement) MPs agree, for Go-live, that the existing process outlined in the ME paper can be followed and will remain in place. ERCOT will consider staggering the Period 3 Interim update deadline when the gray-boxing associated with NPRR146 is addressed. 7/26-Workshop ) MPs acknowledged ERCOT’s limitations before go-live but affirmed preference for system solution after asap after go-live. |  |  |  |  |
| 15 - potentially resolved | 2 | The information submitted into NMMS may be duplicative causing inaccurate models. | Incorrect information will affect LMP prices. | Templates to describe the exact information needed by ERCOT on NOMCRs would facilitate better transition of information need by ERCOT and more accurate modeling information transfer. | 7/20-NDSWG agreement) This concern is with ratings and limits that must be entered consistently in multiple places. 7/20-NDSWG agreement) Short-term for Go-live: ERCOT currently has a process in place to correct known differences. This effort is scheduled to be complete by August 15th. 7/20-NDSWG agreement) ERCOT will redesign existing Line templates to enter data consistently .7/26-Workshop ) ERCOT cannot create pre-populated templates but is restricted to blank templates. 7/20-NDSWG agreement) ERCOT will provide documentation of where the data is used in the form of a whitepaper. 7/20-NDSWG agreement) Long-term: (Post go-live) ERCOT will investigate changes to the operatorship and responsibility of the scada limits. 7/26-Workshop ) Tentatively scheduled for Spring 2011 7/26-Workshop ) Whitepaper on Ratings Usage will be available 7/30. |  |  |  |  |
| 16 - potentially resolved | 2 | There has always been an issue in managing the Network model and outages. Does this problem still exist with Nodal tools? | When submitting model changes into the Zonal Network Model the model change could break approved outages. What has ERCOT done with the Nodal implementations to prevent this from happening? | Explain why this problem existed in the Zonal systems and ERCOT's response on how the system prevents this from occurring or at least how this problem was minimized. | 7/20-NDSWG agreement) This concern is related to the potential for broken outages. MPs agree that in Nodal, the potential still exists, but should occur less often. ERCOT has a manual process (as in Zonal) to check for the occurrence of broken outages in order to prevent problems in Real-time 7.23 ERCOT Outage Evaluator uses the TEID (unique identifier) which shouldn’t change as long as the equipment exists. We will develop instructions to assist MPs in preventing broken outages. 7/23 ERCOT comments) Outage coordination has a report they will use to detect broken outages similar to those used in Zonal this will allow Outage coordination the ability to contact MPs and correct broken outages if they are created. 7/26-Workshop ) MPs continue to be concerned. ERCOT will provide documentation in the ME paper to cover this manual process. 8/18/10 Nodal Engagement Call) The desk procedure that addresses this issue has not been referenced in the ME paper (the ME paper doesn’t reference any desk procedures). The issue will be discussed at the next NDSWG. . |  |  |  |  |
| 17 - SCR | 3 | Where are the published EMS cases for MP review? | In Nodal Protocol section 3.10(8) there is a statement 'ERCOT shall notify each NOMCR requestor when the requested change is processed and implemented in accordance with Section 3.10.1, Time Line for Network Operations Model Change Requests, and ERCOT shall also provide the submitting TSP a link to a Network Operations Model containing the change for verifying the implementation of the NOMCR and associated one-line displays.' When will ERCOT starting providing the TOs with a link to these Network Operations Models for verification of the implementation of the NIOMCR. Also Nodal Protocols 3.10.4 sections; (7) A TSP, with ERCOT’s assistance, shall validate its portion of the Network Operations Model according to the timeline provided in Section 3.10.1. ERCOT shall provide TSPs access, consistent with applicable policies regarding release of CEII, to an environment of the ERCOT EMS where the Network Operations Model and the results of the Real-Time SE are available for review and analysis within five minutes of the Real-Time solution. This environment is provided as a tool to TSPs to perform power flow studies, contingency analyses and validation of SE results. (8) ERCOT shall make available to TSPs, consistent with applicable policies regarding release of CEII, the Network Operations Model used to manage the reliability of the transmission system as well as proposed Network Operations Models to be implemented at a future date. ERCOT shall make the Redacted Network Operations Model available to non-TSP Market Participants, consistent with applicable policies regarding release of CEII as well as proposed Redacted Network Operations Models to be implemented at a future date. ERCOT shall provide model information through the use of the EPRI and NERC-sponsored CIM and web-based XML communications. | ERCOT should implement the required notification so that the TO can verify the implementation of the NOMCR in the operational model. | No last minute fouls ups. How to accomplish this? - 7/20-NDSWG agreement) TSPs currently have access to the full CIM file that is being used in nProd. - The one-lines are not yet posted 7/26-Workshop ) MPs believe that a SOTE environment set up to look at the operations case to be “next” used in production would satisfy this concern. Currently this is not available. MPs will consider an SCR requesting this functionality. MPs would like to see the details associated with the point-to-point telemetry check of models prior to production – resolution undetermined |  |  |  |  |
| Reports |  |  |  |  |  |  |  |  |  |
| 18 - resolved | 2 | When will the State Estimator and Telemetry performance metrics and reports be available? | When will the Telemetry and SE Metrics and Performance reports be available via the Secure MIS? The MPs need this information so they can monitor their performance. | ERCOT needs to start publishing these reports so that MPs can see how they are performing. | Due to the lack of availability of reports, ERCOT has been making many ad-hoc requests for review of telemetry and SE data. 7/20-NDSWG agreement) Five of the SE reports should be available by August 3rd. Two more will be available in September. The quarterly report will be available in Oct. 7/23 ERCOT comments) There are four more SE reports that have recently published to the MIS for June data. They are: · NP3-582 Voltage Residuals vs Telemetry for Critical Buses · NP3-579 SE vs RTCA Base Case for Congested Transmission Elements · NP3-580 SE vs Telemetry for Congested Transmission Elements · NP3-578 State Estimator Convergence Rate There are two SE reports yet to be posted. State Estimator Bus Accuracy Report will post for the first time on Aug 3rd due to the June data being a bit too messy and making the file huge. SE vs Telemetry for Major Transmission Elements should post sometime in the next week, I just need to validate the data 8/11-Nodal Engagement call) Conflicts with PUCT rules prevent two of the SE reports from being published as “Secure” reports. This prevents TSPs from being able to review these reports, but does not prevent TSPs from accessing the SE in SOTE. The ability to access these reports is important for TSPs in order to be able to help validate the model. It was agreed that this item could be closed pending the resolution of NPRR209. |  |  |  |  |
| 19 - resolved | 3 | State Estimator Solution is not getting better. Concern that the State Estimator is very inaccurate. What is the issue from ERCOT's perspective? | If the State Estimator is not matching the zonal trend we will have many problems with LMP prices, as well as operational issues with network and reliability concerns. Decisions on what the model tells ERCOT could result in bad decisions based on invalid information. So ERCOT directives could be contradiction physical condition of the network. | Publish the State Estimator and Telemetry metrics. | ERCOT has been working on the state Estimator and Telemetry metrics reports for months and the TSPs still have not seen them. We do not know if these metrics are being met and what problems exist. We do not want these metrics reports light up on the wall of shame prior to the TSPs being able to see them and have a chance to correct any issues. 7/23 ERCOT comments) (ERCOT response) Though Nodal SE convergence dipped in March due to some issues regarding the modeling of new phase shifters in the system, all other months since CIM-model inception in December have shown an upward trend in convergence. With the exception of one or two reports, all the SE and Telemetry Standards reports that are being delivered for go-live will be available on the MIS after August 3rd. ERCOT will continue to monitor and maintain SE performance. 8/11-Nodal Engagement call) Agreement that the SE results have shown improvement and that this issue could be closed |  |  |  |  |
| 20 - resolved | 3 | There needs to be an exclusion to the Outage Scheduler metrics as related to outages used to manage NOMCR energization. | The ERCOT Nodal Protocols requires the use of the ERCOT Outage Schedule to place New or Relocated Facilities into service. The metrics for this usage of the Outage Scheduler needs to be treated separately from the usage of the Outage Scheduler for operational outages. | Update the reporting metrics. | 8/18/2010 Nodal Engagement Call) ERCOT reported that all outage metrics for Go-live had been gray boxed. There is no accountability for TSPs while the metrics are gray boxed. |  |  |  |  |
| Issues Being Tracked by Other Stakeholder Groups in Addition to TSPs |  |  |  |  |  |  |  |  |  |
| 21 - resolved | 3 | To verify outages have been entered correctly for all segments of a line, each tap station has to be entered in the search criteria. |  |  | 7/23 ERCOT comments) If the MP is using the OS UI, they choose a line they have the ability to list and choose related equipment to that line. This would include all equipment to the next breaker or open device. They would then create a Group Outage on all the equipment chosen. 8/11-Nodal Engagement call) Agreement that the issue could be closed. ERCOT will continue to work to improve the functionality of the OS. |  |  |  |  |
| 22 - resolved | 3 | There is not a “Historical Tracking” of outages. The previous version had {View Update Log}. |  |  | 7/23 ERCOT comments) Unfortunately the core Outage Scheduler doesn’t have this ability in the MP view. If this is required then ERCOT will suggest a report from the OS to assist in audit logging of outage submissions. This won't be included in the OS UI but can be done as a separate report. 8/11-Nodal Engagement call) Agreement that the issue could be closed. ERCOT will continue to work to improve the functionality of the OS. |  |  |  |  |
| 23 - resolved | 3 | Selecting “Time” when entering outages is a click and drag, not a drop down box that worked quite well on the previous version |  |  | 7/23 ERCOT comments) I believe this calendar function was chosen to minimize needed space. The user can also left click the mouse button to move the time forward and control left click to move the time backward. To change this would require a change to every display that uses the calendar. 8/11-Nodal Engagement call) Agreement that the issue could be closed. ERCOT will continue to work to improve the functionality of the OS. |  |  |  |  |
| 24 - resolved | 3 | Custom Filter – “Requesting Company” defaults to TCNPE, the “Operating Company” should, also. If someone needs to change that option, so be it. |  |  | This has been fixed and deployed to NPROD. 8/11-Nodal Engagement call) Agreement that the issue could be closed |  |  |  |  |
| 25 - SCR | 2 | Line segments are not selectable from both terminating substations, moreover, the search pattern is not obvious to users (IE., segment NEWTGF04 between NEW and TGF substations is only available from the (NEW) substation, and missing from the TGF substation). This issue applies to both Human Interface and web services interface. |  |  | There is an outage scheduler list of issues that is owned by market trails. This issue is on that list. 7/20-NDSWG agreement) There is an outage scheduler list of issues that is owned by market trials. This issue is on that list. ERCOT will report back on possible resolutions during the 7/26-Workshop ) NATF workshop. 7/23 ERCOT comments) This defect was deferred. A possible workaround would be: OS UI – Choose the opposite end of the line as the From Station. We will designate business rules for creating the From Station as indicated by MPs. The correction to having both stations show lines will be made post go-live but the method for selecting the from station will be made to match the from station indicated as the near station in the model this will allow the TSPs to use the designated from station as provided in the NMMS model. If this is not available before go-live we will publish a list of from stations to assist the TSPs till this can be corrected EWS - to post a report with the lines and there From and To Station Names. 7/26-Workshop ) MPs feel the workaround is challenging during real-time conditions. MPs will consult with their real-time operations to determine severity. 8/18/2010 Nodal Engagement Call) MPs would like to know what “defect deferred” means. It was noted that this was on the separate OS list. ERCOT provide some clarity on how defects are handled and when they get attention (this one in particular). |  |  |  |  |
| Planning Model Issues |  |  |  |  |  |  |  |  |  |
| 26 - SCR | 4 | SSWG has identified items that need to be incorporated into the Annual Planning Model build process |  | Will require changes to IMM and/or Topology Processor. SSWG has plans to write a new System Change Request and submit this year. | See tab labeled 'All open issues 5-26-10' for all the details 7/23 ERCOT comments) We have identified several “really nice to have items” to add to IMM schema so that it comes across Topology Processor (TP). This is not critical as all items can be added in Model on Demand (MOD). 8/4 Engagement call) MPs feel that individually these changes do not represent great needs, but in total that create enough extra work for MPs that it may jeopardize the entire process. 8/10 ERCOT Planning) Distributive cap/reactors will be a PMCR |  |  |  |  |
| 27 - Resolved | 4 | Annual Planning Model process Go-Live occurs before IMM changes and-or Topology Processor changes are implemented (see issue #1) 8-17 WDW comment) I think this is the biggest question of all the planning issues. It’s potentially resolved as long as all participants agree that any of the three potential resolutions are valid and will be decided by SSWG. |  | 1. Can move forward with new process while making large number of changes until IMM/TP is updated. Or 2. Delay Annual Planning Model Go-Live until changes are implemented, tested, and working. 8-25 CNP comment) Use a different root case for MOD | 7/23 ERCOT comments) Current process has TSP’s starting from scratch every year. New process will yield a base topology to start from and have more eyes looking at base topology. 7/23 ERCOT comments) The changes that will have to be made to that base topology are less than is currently being made and the new process to submit changes is very similar and enables tracking of change submission, which is not available now. 8/17 WDW comments) I do not understand the statement ‘changes … are less than is currently being made’. The current process is that a TSP generally takes an existing base case in PSSE format and makes whatever changes that they deem necessary, usually minor, before sending that data to ERCOT. The new process entails data that is already contained in our base cases and deemed necessary for planning, having to be placed back into the base case. The tracking advantages are a product of using MOD and has nothing to do with using the Topology Processor case as the root case. 8-25 Nodal Engagement Call) Resolved |  |  |  |  |
| 28 – SCR | 4 | What if SCR 759 is not implemented? (SCR 759 is the acLineSegment Name Length Increase in IMM) Topology Processor is still not performing radial line reduction and multi-section line grouping correctly as originally proposed by Siemens Topology Processor will not be able to create planning models that are currently being used for planning models and studies 8/17 WDW comments that the above comment about the Topology Processor should be struck. 8/26/ ERCOT agrees that the Topology is performing radial line reductions as originally proposed by Siemens. | Multi-section line creation will not work properly in building Annual Planning Models | Siemens is supposed to be aware and working on the solution | 7/23 ERCOT comments) The statement “Topology Processor will not be able to create planning models that are currently being used for planning models and studies” means the planning model will not look like the current SSWG case. They will still be valid and can be used. 8/10 ERCOT Planning) The multi-section line will need to be implemented in a PMCR until the line length is addressed after go-live. TSP’s will examine the output from one the cases that will include multi-section lines when the data is certain data is included in the imm and the new TP software in delivered. The software has been tested by ERCOT. 8/17 WDW) Sure they can be used, but not without making lots of changes to the base case so that existing contingency definitions will still work. Rewriting all of the contingency definitions is not a realistic option because it would be a huge step backwards and an enormous amount of work. |  |  |  |  |
| 29 – pending planning resolution | 4 | The actual process for building the Annual Planning Models is still an unknown. It depends on how the IMM/TP is enhanced in the future. | Common assumption is that every quarter new TP download will be planning case starting point, but using new TP download every quarter to start building the cases as of right now would cause an enormous amount of SSWG work. | Will test creating 2010 summer case and 2012 summer case later this year to determine just how difficult this is going to be. | 7/23 ERCOT comments) There is currently no link between the PMCR and the NMCR in the IMM. For some MPs this could result in errors if NMCRs are submitted more than 11 months in advance. Resolution is to live with this for go-live. ERCOT will respond during an upcoming SSWG meeting to explore long-term solutions. 8/10 ERCOT Planning) This will also be addressed on Aug 18 by tsp’s to create an internal process in their company to keep up on changes. |  |  |  |  |
| 30 - NPRR | 2 | Inconsistencies in RARF data versus current planning models. | In new nodal process, RARF data is input into IMM and that data will come out of the TP whether it's correct or not. | NPRR246 is a start that provides a method of getting comments to ERCOT who will ask resources to resubmit the RARF. | Some of this data is very important for TSP planning studies and future project justification. 7/20-NDSWG agreement) ERCOT submitted NPRR246 and is providing comments on NPRR238 to clarify data submission process. 7/20-NDSWG agreement) ERCOT will investigate any data inconsistencies that MPs think need to be investigated after Go-live. The NMG will be the primary point of contact. 7/26-Workshop ) Concern centers around data submittal by REs. Possible solution would be TSP review of some RARF data. ERCOT may have to modify NOMCR submittals in order to make searching for data more feasible. Some sort of tracking mechanism would be useful. Another approach would be to have the RARF submittals sent to the connecting TSP by WCS. |  |  |  |  |
| 31 - pending planning resolution | 4 | Problem with SVCs additions. (Nominal KV error). |  |  | 7/23 ERCOT comments) This is being worked on with Siemens. The voltage schedule will have to be entered in MOD profile. |  |  |  |  |
| 32 - SCR | 4 | FACTS devices modeled as generators and not as desired | The only option may be to change in MOD environment. This should not be a high number. |  | As per 02/03/2010 SSWG Bi-Weekly Conference call all members agreed to modeled the SVCs as generators. It may be more correct/accurate for the Operation Model to represent Statcoms as generators and SVCs as SVCs. This represents the MVaR output on the fill of the Voltage correctly. 7/23 ERCOT comments) The FACTS devices will have to be added into the cases in the MOD environment. |  |  |  |  |
| 33 - SCR | 4 | Assigning cap banks to the right CNG | Some cap banks which are tapped off of lines inside of a substation are modeled connected to their own bus in PSSE. Collapsing these into the correct CNG in the IMM is sometimes difficult. MOD cannot move these from one bus to another in the Control Profile; therefore, the cap bank must be connected to the correct bus in the topology processor output or corrected through a PRJ file in MOD for the Control Profile to be able to adjust the cap bank. |  | 7/23 ERCOT comments) Will not impact CRR as CRR uses DC solution. Primarily a CNP comment. A new CNG can be created. 8/10 ERCOT Planning) Distribution cap banks will need to be added a PMCR. 8/17 WDW) Would be surprised if this was just a CNP problem, but even if so, planning models are developed and modeled so that contingencies mimic real world operation. Potential solution is to allow the use of jumpers in IMM. |  |  |  |  |
| 34 – pending planning resolution | 4 | Assigning loads to the right CNG | Some loads inside a substation may have a hard time being collapsed into the correct CNG. MOD cannot move these from one bus to another in the Load Profile, therefore, the load must be connected to the correct bus in the topology processor output or corrected through a PRJ file in MOD for the Load Profile to be able assign load to the correct bus. |  | 7/23 ERCOT comments) Will not impact CRR as CRR uses DC solution and does not use load. Primarily a CNP comment. A new CNG can be created. 8/10 ERCOT Planning) Distribution loads will need to be added with a PMCR 8/17 WDW) Would be surprised if this was just a CNP problem, but even if so, planning models are developed and modeled so that contingencies mimic real world operation. Potential solution is to allow the use of jumpers in IMM. 8/17 CNP) CNP requested this be a SCR to expand the flexibility of CNG collapsing. 8/25 ERCOT has reservations about this approach and would prefer it be handed with PMCRs. |  |  |  |  |
| 35 - SCR | 4 | Zero impedance lines created by TP have default 9999 MVA ratings |  |  | 7/23 ERCOT comments) Zero impedance lines model breakers and switches within a substation. In IMM, the Switch/Breaker model does not have rating. This seems to be OK in the operations environment. This can be modified in MOD to add correct ratings where they are important, which is not every instance. 8/10 ERCOT Planning) An SCR will be needed if we want rating on these otherwise the MOD will need a PMCR 8/17 WDW) Have no idea why this is OK in operations environment, but to not take equipment ratings into account is a bad idea and seems to me to even violate NERC FAC standards |  |  |  |  |
| 36 – Pending Planning Resolution | 4 | Load ownership assignments, including zero impedance branches created by TP | The Owner Number/Name data for the load is incorrectly propagated by the TP. |  | 7/23 ERCOT comments) This is being worked on with Siemens. Not critical. |  |  |  |  |
| 37 - resolved | 4 | Generator Pmax and Pmin | IMM contains limits for generators from RARF data. The RARF data used currently is HR_LMT for Maximum Operating MW and LR_LMT for Minimum Operating MW. These come across TP as Pmax and Pmin |  | HR_LMT and LR_LMT in most cases are clearly unreasonable values to use for planning cases. Pmax and Pmin can be set by the generator profile in MOD, so SSWG does have that option for creating the planning cases. However, SSWG would recommend the ERCOT Network Modeling group use something more reasonable to populate in IMM. 7/23 ERCOT comments) This will be added in MOD with the dispatch. |  |  |  |  |
| 38 - SCR | 4 | Cap banks on distribution voltage instead of modeled on transmission level bus | Is this a problem if distribution caps are reflected in station power factors? |  | 7/23 ERCOT comments) Must be added in MOD as they are not modeled in IMM. Considering adding schema to IMM to store this value. 8/10 ERCOT Planning) A PMCR is needed for distribution CAPS 8/17 WDW) There are hundreds of these missing cap banks |  |  |  |  |
| 39 - resolved | 4 | Distributed generation modeled instead of negative load | Modeling distributed gens should not be a problem |  | 8/10 ERCOT Planning) A PMCR is needed for distribution generators The distribution generators are not modeled in operations |  |  |  |  |
| 40 – pending planning resolution | 4 | Specific models added for contingency analysis, dynamics analysis, or short circuit analysis | Can some of this be done in-house after case creation - short circuit? Are the mutual-coupling concerns for sequence data due to use of old program that may be updated? This is only used in SPWG cases. (WDW Note: I am not talking about adding sequence data to the cases. I am pointing out some buses are created for planning study purposes without being associated with any particular node.) |  | As far as short circuit cases are concerned, SPWG will not be using SSWG cases as their base cases as far as we know. SPWG will still be building the cases from scratch using PSSE. 7/23 ERCOT comments) SPWG has decided to use ASPEN. 8/10 ERCOT Planning) SPWG does not use SSWG for building their cases. SPWG has decided to use ASPEN. 8/17 WDW) This punishes TSPs who have made a concerted effort to align their base cases to serve the needs of planning, protection, and stability studies without having to maintain separate cases. |  |  |  |  |
| 41 – pending planning resolution | 4 | Autotransformer differences Op model vs. Planning model |  |  | 7/23 ERCOT comments) This is not an issue but a choice that each TSP has to make to model autotransformers. CNP uses a different model for Ops to help their Operators but wants the real model in planning. Must be consistent between the two models. 8/10 ERCOT Planning) If a transformer is modeled as a three winding in planning and operations have a two winding, the planning will see a 2 winding from TP. Each company will need to work with their operation for modeling. 8/17 WDW suggested this is an SCR resolution. ERCOT disagrees. TSPs need to make a decision on how the transformers are modeled. It should be the same for both Operations and Planning. |  |  |  |  |
| 42 – pending planning resolution | 4 | Phase Shift of autos for short circuit studies | Topology processor does not include phase shift data (30 deg) placed for short circuit calculations |  | 7/23 ERCOT comments) This will have to be added in MOD. 8/10 ERCOT Planning) This will have to be added in MOD with a PMCR. 8/17 WDW) Seems like adding schema to IMM to store this value would work better and not be particularly intrusive. Again, this punishes TSPs who have made a concerted effort to align cases to serve the needs of both planning and protection analyses. |  |  |  |  |
| 48 – Pending Planning Resolution | 4 | Issues with Topology Processor 8.0: (1) still not performing radial line reduction properly (2) off-nominal 3-winding transformer impedances not being calculated correctly (WDW 8/17/10) | Additional work for TSPs to fix the topology so that cases can be created that studies can be performed on. | Discuss with ERCOT and Siemens. Needs to be fixed. |  |  |  |  |  |
| 49-Pending Planning Resolution | 4 | Modeling data included which is associated with SPS or RAPs not actual equipment | TSPs not sure what to do with these since they are not modeled in planning cases | Eliminate this modeled equipment from IMM |  |  |  |  |  |
| 50 – Pending Planning Resolution | 4 | IMM and Topology Processor need to be developed with the idea that power flow software is enhanced with major changes typically every two to three years | TSPs can’t use future enhancements because IMM and-or TP doesn’t have the capability, or TSPs will have to plug the data back in through MOD (Fixed shunts are a good example of this) | TP and IMM need to be converted to output PSSE 32 and then from time to time in the future as power flow software enhancements are made |  |  |  |  |  |
| 51 – Pending Planning Resolution | 4 | TSPs that do not have access to PSSE or MOD File Builder | How do they create PMCRs | New version of MOD is supposed to include MOD FileBuilder; therefore, this may no longer be a problem. However, when will that be delivered? | 8/26 ERCOT) It is important that TSPs and ERCOT each have the tools necessary to complete SSWG work. |  |  |  |  |
| Grey Box |  |  |  |  |  |  |  |  |  |
| 43 – gray box | 2 | Based on NPRR219, additional and unknown PUN modeling and outage scheduling is a large burden on the TSPs. | Potential support PUN (behind the fence) model in the TSPs' EMS systems to ensure reliable monitoring of statuses. | Future grey boxed enhancement in Outage Scheduling allowing REs to enter their own outages. Also, the metrics need to be changed for outage scheduling. | 7/20-NDSWG agreement) This is a future gray boxed enhancement in Outage Scheduling allowing REs to enter their own outages. For go-live, ERCOT will gray-box (will not post publically) reports that are influenced by this responsibility. The PUCT and TRE have been contacted and are in agreement. The long-term post Go-live resolution will be an enhancement to allow REs to enter their own transmission outages. |  |  |  |  |
| 44 – gray box | 3 | NPRR146 implementation plan and schedule for implementing grey box changes | Allows for shorter lead time when submitting ICCP information for telemetry objects. | The NPRR was approved with grey boxed language. Need a plan for how these change we be un-grey boxed and implemented after go-live. |  |  |  |  |  |
| 45 - potentially resolved | 3 | NOGRR034 Rescind Telemetry Performance Calculation Exclusions | Compromise was to grey box future development of a Planned RTU outage tracking method to remove associated points for Telemetry standard performance metrics. |  | 7/23 ERCOT comments) NOGRR034 issues should all be resolved by the fact that NDSWG will be revising the telemetry performance metric. There is a conference call scheduled for Monday Aug. 2nd to discuss 8/18/2010 Nodal Engagement Call) Resolution pending final TAC approval of the telemetry standards revision. |  |  |  |  |
| 46 - NPRR | 3 | Grey Box items and additional upgrades need some kind of guarantee that they will be completed in a timely manner. | TSPs have increased manpower and our workload due to the fact that several protocols and business processes were designed to be done by ERCOT. However the systems do not have the capability envisioned in the original design. The results is instead of ERCOT performing these functions, 17 different TSPs are performing these functions at a much higher cost to TSPs than anticipated. |  | 8/8/10 ERCOT) ERCOT has a process in place so that Stakeholders can assign priority to gray box items. An NPRR could provide MPs a guarantee of when the items are processed. |  |  |  |  |
| 47 – ME paper | 2 | TSPs do not want to be responsible for the modeling of pseudo equipment in NMMS as prescribed by the current ERCOT business process. |  |  | 7/20-NDSWG agreement) MPs would like to wait until 7/26-Workshop ) NATF meeting to decide upon a resolution. Possible resolutions: - Proceed with the ME process for TSPs to model pseudo devices – no Protocol changes - TSP sponsored NPRR to place the responsibility to model pseudo devices on ERCOT. 7/26-Workshop ) MPs agree that the Pseudo modeling portion of the ME paper should be struck because is contrary to Protocols because it makes a requirement where none exists. Suggested Replacement “TSPs may use Pseudo equipment if desired, but their use will not impede equipment being energized into service.” MPs request ERCOT to redraft the Supplement Load section to provide more detail including the process of requesting the Sup. Load and approval |  |  |  |  |
| Parking Lot |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Parking lot items and additional upgrades need some kind of guarantee that they will be completed in a timely manner. | TSPs have increased manpower and our workload due to the fact that several protocols and business processes were designed to be done by ERCOT. However the systems do not have the capability envisioned in the original design. The results is instead of ERCOT performing these functions, 17 different TSPs are performing these functions at a much higher cost to TSPs than anticipated. | Set funding aside for parking lot items. |

- PRIORITY KEY

1 = Show stopper; Needs resolution before Go-live can be accomplished.

- 2 = High priority issue that should be resolved by Go-live

3 = Needed but can be implement post Go-live

4 = Needed by Planning Go-Live (approximately March 2011)