## DAM Issues List
Issue # | Issue Title | Contingency & Overload Pair (Date Observed) | DSV | Date Submitted | Submitter | Category | Mkt. | Priority | Issue Description | Assigned To | Status | Estimated Resolution Date | Comments
48 | Stress Test update | [8 empty] | Moorty/Mereness | Stress test update |  | [ERCOT 8/19] Stress test scenario to be copied into nProd for Aug 21 to allow market observation. More work being done to consider study of: - DAM solution where monitored, but not secured at the 69kv line level - DAM solution with tool from vendor to unsecure radial loads that can't be solved by generation [ERCOT 8/24] Test not completed in nProd this past weeken due to difference in data and environments created issues with "stress test DAM". Planning to repeat this coming weekend- Sat/Sun DAMs for constrained and unconstrained test. [ERCOT 8/26] Confirming "plans to" run stress scripts in DAM for weekend, OpDays Aug 29/30 Internal stress testing focusing on: - Excluding constraints due to radial load pockets (base case and contingency) - MMS5P9 / Sept - Monitor-only (not secure) of 69-kV and below (running on nProd cases) - MMS5P9 / Sept [ERCOT 8/31] Stress test in nProd did not yield desired results due to curtailment of offers by COPs Unconstrained solution procured 52,900, followed on Sunday by 52,300 with network constraints Deep Dive request to look test regarding LaMarque-Stewart, Kennedy Switch, WDenton-FtWorth, and EnnisCreek constraints [ERCOT 9/2] Reports from stress test should reflect (as best possible) what ERCOT posts after every DAM: Reports: DAM Hourly LMPs, DAM Settlement Point Prices, DAM Shadow Prices, DAM Total Energy Purchased, DAM Total Energy Sold, Hourly load forecast by load zone used in the test
28 | Adverse impact on DAM performance due to large number of CRR Offers |  |  | 2010-08-05 | ERCOT | Market Design | DAM | 1 |  | Steve Reedy | Active |  | [ERCOT 8/12/10] Mereness- MMS system enforces NOIE CRRs to be less than 110% Load ERCOT Board update to consider limiting PCRR Options in DAM via NPRR. [ERCOT 8/23] Potenetial NPRR- meeting with NOIEs to consider limits or limitation to PCRR paths (107) [ERCOT 8/31] DAM stress test Monday with 126 distinct paths- still looking at results to determine if 4 hour execution based on only CRR Offers or other factors. [ERCOT 9/2] OD 8/31 - 126 paths OD 9/1 - 114 paths OD9/2 - 164 paths DAM is implemented as a iterative process between an optimization phase and network analysis (powerflow and contingency analysis). For contingency analysis for CRR Offers, each distinct source/sink combination has to be analyzed separately. For example, the total number of CRR Offers submitted is 500. These 500 contain 100 distinct source/sink combinations. The number of contingencies to be analyzed is 2500. This leads to a total of 100*2500=250,000 powerflow executions. At present we expect the average number of iterations to be 7-8. To meet the DAM timeline we expect the network analysis to take 5 minutes for each iteration, optimization to take around 15 minutes at the most. We can meet the netowrk analysis timeline if the number of distinct source/sink combinations for CRR Offers are around 150 and the number of contingencies to be analyzed is 2500. If the number of distinct source/sink combinations exceeds this then network analysis timelines will dramatically deteriorate.
5 | Total Energy Sold/Purchase & PtP |  |  | 2010-06-11 | LUME | Reports | DAM | 1 | The DAM Total Energy Purchased and DAM Total Energy Sold reports don't include awarded PtP Obligations and Options. To fulfill the Protocol requirements of 4.5.3 (2) (f-g) all energy purchased and sold at each Settlement Point in the DAM, including PTP obligations should be included in these reports or in an alternative report(s). Seperately, another report that describes those NOIE CRRs options not redeemed in the DAM and held as an option into Real Time is needed. | Mereness | Pending Report | ? | [ERCOT 8/12/2010] Mereness asked team to create prototype- single DAM Awards report with column layout: (See Sample DAM Report Worksheet in this workbook) DAMDate Hour SettPt EnergySold (Sum cleared: 3PSO + EOnlyOffers) PtPObligations Source cleared CRR-Source (NOIE CRR Offers minus cleared) EnergyPurchased (Sum cleared of Energy Bids) PtPObligations Sink cleared CRR-Sink (NOIE CRR Offers minus cleared) [Mereness action] Target release this week 8/23 for new report prototype. [ERCOT 9/2] - Redacted version sent, cross-checking with 3 NOIEs isolated by data to release un-redacted version.
61 | Specific issue of LMPs/awards in Silas Ray | OD 8/19 For the binding cosntraint at hour 24, DAUSLOS5___AUSTRO_AT1H______________________AUSTRO___345.0_AUSTRO_____1.0_X, | [6 empty] | Incorrect LMP calculation under specific circumstances. | MMS5-P9 | Software |  | [ERCOT 8/24] - ABB issue under a very specific scenario. New SPR created and fast tracked for Sept delivery. Error in the shift factor used in the NSM post-processing to calculate electric bus LMP . The bug is effective when in the contingency simulation, a new bus is created due to the bus split and the new bus is FROM bus of the binding constraint that has been sent to NCUC. Since the new bus has no bus name in the post-processing, NSM cannot find the match with the FROM bus of the existing constraints and incorrectly change the sign of the shift factor. [ERCOT 8/26] - has been addresses with MMS5P9 / Sept
62 | DAM Credit for 3PSO | [7 empty] | Non Business Day credit adjutment uses 95% of RT-DAM positive differences in prices |  | Software- Credit discussion |  | [ERCOT 8/24] - CYager taking to MCWG this week, NATF next week. Considering change to calculation for 3PSO. [ERCOT 8/26] - 1pm meeting at Met today 8/26 [ERCOT 9/2] - NATF approval to change 3PSO and Energy Only Offers for go-live
63 | LDF Reports | [7 empty] | Mismatch report between LDF and what is used in MMS |  | Software- LDF integration |  | [ERCOT 8/24] - under investigation to find source of problem [ERCOT 8/26] - verified correct in MMS, but not in MIS report.
64 | LDF in DAM using SE | [7 empty] | Planning to seed LDF with State Estimator values in nProd environment this week to improve LDFs (such as remove zeros) that impact certain busses and surrounding busses. |  | Testing |  | [ERCOT 8/24] Plan to enhance LDF with State Estimator seeding for Thursday Aug 26 DAM Op day [ERCOT 8/26] Confirming this enhanced LDF has been done in nProd for Aug 26 but refining needed to more load DEEP DIVE AI- send SE values, and missing list in LDF (Reviewing file from Freddy Garcia) File has confidential Load Values in it and is not being distributed.
46 | PSSe File Request | [9 empty] | Active |  | [ERCOT 8/12/2010]: Delivered for 8/4/2010 - 20 CDs delivered to 20 companies [ERCOT 8/20/2010]: Delivered for 8/4/2010 - 20 CDs delivered to 20 companies DSV 23 goes in Sept 1- look to release PSSe by Friday - Tools identified to reduce effort (but is still manual, not for post-go-live, and will be mailed or hand-delivered) - ERCOT targeting to release PSSe with subsequent model loads in Aug/Sept - PSSe file request for DSV 23/Sept 1 model Load to be created and sent via mail to 21 companies.
8 | Congestion on Cedar Crest - Compton 69 kV line | SCDHSOR8 3890__A CDCSW 69 CMPST 69 (06/15/10), SINDCDC8 3890__A CDCSW 69 CMPST 69 (07/31/10) SCMPIND8 3890__A CDCSW 69 CMPST 69 (08/13/10) SCMPIND8 3890__A CDCSW 69 CMPST 69 (08/15/10) |  | 2010-06-15 | LUME | Misc. Error | DAM | 1 | This line is modeled on a radial-feed in both the SSWG cases and the Operations load flow model, and therefore should not overload under contingency conditions. | sai | Active |  | ERCOT researched this and found that it was an incorrect contingency definition and invalid load throw over constraint had been identified as the root cause and had been fixed (reported at 7/29 NATF mtg). Issue still shows up in 7/31/10 DAM. When will Network model get corrected? [ERCOT 8/6/2010] Can luminant provide the contingency name and overloaded element as it appears in the DAM reports. With the contingencies being auto-generated and the name not beig consistent till DSV22 - it is going to be a challenge to track and confirm if contingencies are being correctly defined. For DAM OD 7/31 - it appears that the contingency in question is SINDCDC8 and this caused the overload of 69 KV line 3890_A from cedar hill to sorcey road. [LUME 8/10/10] the contingency causing this overload in the DAM for 7/31/10 was Industrial Blvd - Cedar Crest Sw. 138 kV line [ERCOT 8/12/10] Has not re-occurred since 7/31/10, but continue to monitor [LUME 8/16/10] This constraint was active again on 8/13 & 8/15, so it is still an active issue Aug 19- Meeting thoughts - Load rollover definition vs Operator action- utilize Oncor / David Bogen for confirmation. 1- LDF research 2- amount of load moved is 100% by rollover scheme - Needs to be 10-15 range [ERCOT 8/18/2010]CDCWM-CMPST(69KV) is a radial line connecting to load at CMPST 69KV and WALST 69KV for contingency SCMIND8. The contingency SCMPIND8 : two 2 138 KV lines outaged: INDST-CMPST, CMPST-CDCSW: caused load at CMPST 138KV 100% rollover to CMPST 69KV. The total loading at station CMPST 69 and WALST 69 caused CDCSW 69 to CMPST 69 to become binding. The DAM awards at solution of DAM OD 8/15 hour 21 is as following – Load at CMPST (138 KV) = 16.2 MW / Load at CMPST (69KV) = 30.2 MW Load at WALST (69 KV)=25.5 MW / LineFlow CMPST - WALST (69KV) = 25.6 MW LineFlow CDCWM-CMPST(69KV) = 55.8 MW - binding at 72 MW for contingency SCMPIND8. Line limit CDCSW-CMPST (69 KV) = 72 MVA – after contingency load rollover causes this line to be binding - 138KV LDF1 rolls- over to 69KV LDF2 - both at CMPST The LDF between hour 15 and 24 of these stations are LDF MW 15 MW 16 MW 17 MW 18 MW 19 MW 20 MW 21 MW 22 MW 23 MW 24 CMPST_LDF2(69) 2.84 2.62 6.17 3.94 4.11 6.16 9.55 3.23 5.1 4.41 CMPST_LDF1(138) 11.43 11.62 11.81 11.12 10.95 10.82 10.76 10.74 11.41 10.28 CMPST_CMPST_LD2(138) 0.03 0 0 0 0 0.01 0 0 0 0 CMPST_CMPST_LD3(69) 10.33 10.41 10.34 10.33 9.91 10.43 10.57 10.7 10.31 10.11 WALST_LDLXFMR2(69) 9.03 9.1 9.05 6.43 8.5 8.46 8.63 8.68 8.5 8.16 WALST_LDLXFMR4(69) 2.7 2.65 2.58 2.7 5.14 2.78 8.38 8.22 7.86 7.57 [LUME 8/24/10] LUME will discuss a brief PowerPoint presentation on the 8/24/10 conf. call to show findings of our LDF/ analysis on this issue. [ERCOT 8/24] a) it looks like there is a one hour skew between what you are getting in the reports versus what DAM is using in terms of LDFs – we are investigating to see whether it is a reporting issue or an bug in MMS when it is reading the LDFs – for example in slide 4 – the LDFs you have highlighted in yellow – correspond to hour ending 22 in DAM b) there may be a misunderstanding of the N4 contents in the spreadsheet. The MW values given for the loads are AFTER load zone MW distribution using the LDFs, therefore the MW values of 46.4 MW total in Compton station is after the load zone MW is distributed down – it will NOT match the LDF – LDF is just a scaling factor and expecially with large amounts bid in at the load zone – one can expect higher MW at the load ERCOT review of the powerpoint presentation leads to i) there is a skew of one hour in the posted LDFs versus what is used in DAM – investigating to see whether the problem is in the report or in MMS. ii) If item i) above is due to the one hour skew then the real issue is the quality of LDFs
9 | Congestion on Seguin - Seguin West | DMARZOR5 428T428_1 SEGUIN 138 SEGUWE 138 (05/21/10), DCLEZOR5 428T428_1 SEGUIN 138 SEGUWE 138 (07/15/10), DMARZOR5 428T428_1 SEGUIN 138 SEGUWE 138 (08/04/10) | 21 | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Fayette, Gideon, Hays, Lost Pines, & Rio Nogales (see 7/19/10 NATF presentation for more detail) | sai | Active | ? | Between 5/21 & 7/15, bound 27 days in Nodal and 3 days in Zonal. It is unclear whether this is a model quality problem or simply a difference in how Nodal flows will differ from Zonal. LUME developing RAP for ERCOT consideration. [LUME 8/12/10] - between 5/21/10 and 8/11/10, this line has constrained on 51 seperate days. We continue to believe that there is something counterintuitive going on in the Nodal DAM model in this area that needs to be better understood and corrections made as appropriate. [ERCOT 8/15/2010] For DAM OD 7/13 the cause of the high shadow price was due to incorrect contingency SCDHSOR8 couple with a load rollover scheme that resulted in a high radial load pocket on this contingency. For DAM OD 8/11. constraint SEGUIN 138.0 SEGUWE 138.0 under contingency SSMIMCQ8: SSMIMCQ8 is a single line outage contingency. The outage element is the line from SMI to MCQUEE. The overloading line is the line from SEGUIN to SEQUWE with large shadow price. Once the line from SMI to MCQUEE is out, the line from SEGUIN to SEQUWE becomes a radial line that serves the loads SMI_T8, SEGUWE_SEGUWET1 , SEGUWE_SEGUWET2, SMI_SMI_T7, SMI_SMI_T1, SMI_SMI_T6, CAPERP_CATERPT2, and CATERP_CATERPT1. Thus for this binding constraint, only LZ_LCRA and LZ_SOUTH has nozero shfit factor -- the sum of LDF of individual loads. Analyzing other cases to determine of overload. [LUME 8/16/10] What DAM model corrections need to occur to correct the modeling issues described by ERCOT for the 8/11/10 DAM (see ERCOT's 8/15/10 comments)? Additionally, does ERCOT have an explanation of what is causing the XMAR58 (8/13/10), DMARZOR5 (8/13 & 8/15), and SSHEMAR8 (8/17) constraints to result in overloads of this line? Deep Dive 8/19- Not a radial load pocket, shadow prices not unreasonable, but significant generation movement. LUME to continue work. Steel mill distribution? DAM reflects all load as conforming with respect to LZone/LDF. [ERCOT 8/18/2010]For the DAM binding constraint 428T428_1 from SEGUIN 138 to SEGUWE 138, the contingency SSMIMCQ8 forms a load pocket (i.e. only load zones LZ_SOUTH and LZ_LCRA have impact), but other contingencies such as DMARZOR5, XMAR58, SSHEMAR8 and SCIBMAR8 don’t form load pocket (i.e. both load zones and resource nodes have impact). The constraint 428T428_1 is at the boundary of two area thus it get impact from both sides of generations and loads if a load pocket is not formed. Shadow price for XMAR58 - $33 to $242 Shadow price for DMARZOR5 - $3-$322 Shadow price for SSHEMAR8 - $1072 Shadow price for SCIBMAR8 - $46$400 For contingencies XMAR58, DMARZOR5 & SSHEMAR8 many resources had shift factors from -0.09 to 0.05. The load zones (in some hours all of them - but mostly LZ_SCPS & LZ_SOUTH) also had non-zero shift factors - ranging from -0.09 to 0.02.
10 | Congestion on Round Rock - Round Rock NE | DHUTGIL8 1660__A RRNES 138 RNDRK 138 (07/21/10) |  | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Sandow (see 7/19/10 NATF presentation for more detail). LUME submitted 3 RAPs to ERCOT/Oncor for consideration on 7/14/10 | John Adams | Active | ? | Between 6/18 & 7/15, bound 7 days in Nodal and 15 days in Zonal. This seems like a legitimate constraint that is binding on a repeated basis and consistent with the directives in Section 3.10.4 (6) of the Nodal Protocols, may benefit from additional operational intervention or system monitoring while longer term line upgrades are pursued. [ERCOT 8/5/2010] - RAPs received at ERCOT - under review (still under review-JA) [LUME 8/10/10] With the correction of the previously invalid line rating of Hutto - Round Rock NE that occurred on 8/18/10, congestion on this element substantially increased beginning with the 8/19/10 DAM. Thus approval of the 3 RAPs submitted by LUME on 7/14/10 or some alternative RAPs that ERCOT and/or Oncor develop are needed. [JADAMS8/24] - Regarding 2 RAPs, TSPs not creating a higher 15-min rating than the existing emergency rating (AEN/LCRA). Oncor objection on 3rd RAP. ERCOT - 8/31 Item 10 (Congestion on Round Rock – Round Rock NE) ERCOT Operations implemented the proposed RAP for this line in its real-time (EMS) systems late Friday (8/27/10) evening in both Nodal and Zonal systems. A NOMCR is in the works to get this added to NMMS so that it can be implemented in MMS.
11 | Congestion on Mc Neil - Summit | SMCNMAG8 CKT_907_1 MCNEIL 138 SUMMIT 138 (07/17/10) |  | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Sandow (see 7/19/10 NATF presentation for more detail) | sai | Active | ? | Between 5/12 & 7/15, bound 17 days in Nodal and 0 days in Zonal. It is unclear whether this is a model quality problem or simply a difference in how Nodal flows will differ from Zonal. LUME developing RAP for ERCOT consideration [ERCOT 8/6/2010] As per ERCOT analysis presented at NATF - did not find any network model issues. However the DAM dispatch is quite different from Zonal RT dispatch. Suspect due to offer/bid submission patern for Nodal DAM. [LUME 8/10/10] Can ERCOT please offer some supporting analytical evidence that the principle cause of the dramatically higher flows reported on this line at the 7/29/10 NATF meeting are indeed due to odd offer / bid submission by performing analysis such as was presented at the 8/5/10 Nodal DAM Deep Dive for the Pearsall - Derby constraint?
14 | Congestion on Victoria - N. Victoria 138 kV line | SVICMAG9 N_VICT_VICTOR1_1 VICTORIA 69 N_VICT 69 (07/17/10) |  | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/19/10 NATF presentation for more detail) | John Adams | Active | ? | Between 5/4 & 7/15, bound 12 days in Nodal and 0 days in Zonal. ERCOT has a MP in place in Zonal to control overloads on this line. How can this MP be reflected in DAM to provide a comparable treatment of this congestion management in Nodal DAM and RT as Zonal RT?
15 | Congestion on Trinidad - Winkler 138 kV line | SJEWPLS8 1240__K TRSES 138 WINKLER 138 (07/17/10), XJEW58 1240__K TRSES 138 WINKLER 138 (08/10/10) | 21 | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting North Load Zone (NLZ) to North Hub spreads (see 7/19/10 NATF presentation for more detail). RARF update to mark this load as self serving | ken ragsdale | Model Updates | ? | Between 5/4 & 7/15, bound 12 days in Nodal and 0 days in Zonal. ERCOT and LUME identified at the 7/29/10 NATF meeting that this is and 'end-to-end' line loading problem associated with an improper load distribution to the load serving busses along this line that contains Big Brown startup / standby load that should not be placed on this line. What needs to be done to get this corrected in the Nodal Model? Change Load to be zero in RARF- issues still to discuss versus systemic (psuedo measurement for SE)
16 | Congestion on Ennis Creek 138/69 kV auto | BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/13/10) BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/14/10) BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/15/10) BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/16/10) BASE CASE ECRSW_FMR1 ECRSW 138 ECRSW 69 (8/17/10) | 21 | 2010-07-19 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting West Load Zone (WLZ) to West Hub spreads (see 7/19/10 and 7/29/10 NATF presentations for more detail) | sai | Pending Closure - Radial Load Pockets | ? | Between 6/5 & 7/15, bound 16 days in Nodal and 0 days in Zonal. ERCOT identified and reported at the 7/29/10 NATF meeting that this is issue is being caused by an improper breaker status in the Nodal model that is shown as closed, which is shown as open in Zonal. What needs to be done to get this corrected in the Nodal Model? [ERCOT 8/11/2010] ONCOR confirmed the breaker status is normally closed. The only equipment that is normally open is line 6765_D and both Nodal and Zonal databases are the same. PI data also shows flows and no outages on the 138/69kv transformer from 6/5 to 7/15. Base case violations on the Ennis creek 138/69 KV auto is showing frequently in the DAM runs. The cause is that this transformer is feeding a radial load pocket and the normal rating of this transformer is 24 MVA. The two radial loads LDF are OK (compared to PI data). Also, it appears that TSP confirmed that the rating of this transformer are correct 24/28. One additional piece of information is that the lines at the 69 KV are rated at nearly twice the transformer rating. Based on this information – this issue can be closed? [LUME 8/16/10] Between 6/5/10 and 8/17/10, this constraint has bound on 31 different days in the DAM and has accumulated >$71M of congestion, does ERCOT have any explanation for what is causing this chronic congestion associated with a Basecase (N-0) overload? [Dive Mtg 8/17] - Although issue associated with Radial Load pocket- desire to ensure that is the only issue since it is binding every day, and up to $17 million in cong costs
22 | Congestion on Elkton 345/138 kV auto | DTRCELK5 ELKTN_MR3L ELKTN 1 ELKTN 138 (08/10/10) DTRCELK5 ELKTN_MR3L ELKTN 1 ELKTN 138 (08/12/10) DTRCELK5 ELKTN_MR3L ELKTN 1 ELKTN 138 (08/13/10) DTRCELK5 ELKTN_MR3H ELKTN 345 ELKTN 1 (08/16/10) DTRCELK5 ELKTN_MR3L ELKTN 1 ELKTN 138 (08/16/10) | 21 | 2010-07-29 | LUME | Modeling | DAM | 1 | Congestion on this auto appears to be caused by a double element contigency (N-2) that is not a valid double-circuit contigency per Oncor (see 7/29/10 NATF presentation for more detail) | ? | Pending Closure- Conting DSV23 | ? | Lumiant Energy understands that Oncor is in agreement that an incorrect double-circuit contingency defintion (DTRCELK5 - Martin Lake - Tyler Grande / Elkton - Forney) is being used and will be filing a NOMCR to correct this [ERCOT 8/5/2010]: same popped up during LFC test on 8/4. online correction was made to EMS. Need to confirm future DSV releases have fixed this issue. [ERCOT 8/11/2010] The double circuit contingencies DFORFRN5 and DELKMLS5 have been removed by ERCOT/AG in NOMCR 6443_1 set to energize on 8/14/2010. DSV23- 9/1/10 [LUME 8/16/10] According to our research of the DSV21 contingency definition file: * DTRCELK5 (Martin Lake - Tyler Grande / Elkton - Forney) continues to be an invalid double circuit contingency and needs removed ASAP * DFORFRN5 (Forney Sw. - Forney Power Partners Dbl. Ckt.) is an invalid double circuit contingency in that it is only 0.10 miles long (i.e. < 0.5 mile criteria for valid dbl. ckt.) and needs to be removed ASAP * DELKMLS5 (Martin Lake - Elkton / Martin Lake - Tyler Grande) is a valid double circuit contingency and should not be removed from the contingency definition [Dive mtg 8/17] - ERCOT to provide details/confirmation for Martin Lake area contingencies
25 | Congestion on Tenaska - Concord 138 kV line | STENGDV8 TEN_CRD2_1 TEN 138 CRD 138 (07/21/10) |  | 2010-07-29 | LUME | Modeling | DAM | 1 | Congestion on this line seems to be negatively impacting Tenaska Cleburne (see 7/29/10 NATF presentation for more detail) | ? | Pending Closure | ? | [ERCOT 8/5/2010] No issues found with network model. There are two lines between Tenaska and Conord: TEN_CRD1_1 and TEN_CRD2_1. The contigency is to out the line TEN_CRD2_1. [LUME 8/12/10] - overloads on this line have bound on 26 different days in the Nodal DAM trials between 6/30/10 and 8/10/10 and is negatively impacting the Tenaska Cogen plant in a way that is inconsistent with what has been observed in Real Time. Lumn talking with Tenaska- may lower and eventually remove [ERCOT 8/12/2010] DAM OD 7/28 The contigency definition of S_1089 is: There are two lines between Tenaska and Conord: TEN_CRD1_1 and TEN_CRD2_1. The contigency is to out the line TEN_CRD2_1. The binding constraint is at the line TEN_CRD1_1. The base case flow on these two lines are 92MW and 180MW, respectively. S_1089 TEN_CRD1_1 TEN 138.0 CRD 138.0 Using Hour 17 as an example, the dominant contributors to the post-contigency flow are: TEN_CC1_1 with 196MW, an energy only offer at settlement point TEN_CT1_STG with 100MW, and a PTP bid source at the same settlement point TEN_CT1_STG with 100MW. The total injections of these three control variable are 400MW. The shift factor for these three resources is 0.759. Since the binding contigency constraint shadow price is about 30 $. With shfit factor of 0.759, the binding constraint itself can bring down the LMP at TENASKA by 30*0.759 = 24 $. Since HB LMP is average of 345kv hub bus LMP and the constraint is at 138KV, LMP at TENASKA is lower than HB_NORTH LMP. [DIve mtg- 8/17] - Chronic congestion that is not sensible- ERCOT asked if same bid/offer being submitted that is overloading day-after-day
29 | ERCOT identifies self serve load and marks them in the CIM |  |  | 2010-08-05 | ERCOT | Modeling? | DAM/RUC | 1 |  | John Adams/Ken Ragsdale | Active
32 | LFC Test 8/4/2010 - double circuit contingecny 345KV sandow to temple caused overload of HEARNE Auto. |  |  | 2010-08-05 | LUME |  |  | 1 | Need 15 minute ratings data on HEARNE auto in order to implement RAP | John Adams | Active
35 | Congestion on Navarro - Richland 69 kV Line | SAMGJEW8 2310__C NVARO 69 RCHLD 69 (08/10/10) | 21 | 2010-08-11 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting North Load Zone (NLZ) to North Hub spreads. | ? | Pending Closue- DSV24 Contingency Issue | ? | [LUME 8/12/10] this constraint has occurred on 6 separate occasions between 7/27/10 and 8/11/10 and is typically associated with extremely high shadow prices (e.g. >$200,000). When this constraint is active, North Load Zone blows out over North Hub. [ERCOT 8/12/2010] DAM 08/05: Contingency SAMGJEW8 casuing overload from NVARO to RCHLD. Shadow price=97304 for HE 17.This contingency outages 1220_C and a bunch of lines (looks like multi sectional lines). Contingency causes a radial feed of loads from line between NVARO to RCHLD (69 KV 2310__C). Rating at hour 17 is 36 MW. It feeds the following radial loads - RCHLD_LD2101, COLDG_LDLXFMR2,COLDG_LDLXFMR1,WRTHM_LDLXFMR1,GRSMN_LDLXFMR1,MEXIA_LDLXFMR1,WTGLF_LDLOAD1 [LUME 8/18/10] An "end-to-end" line loading assesment was performed in the SSWG 2010 Summer Planning case to determine whether overloads of this line seem to be a true irresolvable constraint from a physical perspective or a LDF issue in the way the DAM is allocating the load. In the SSWG case, loading of this line is only 85% of its rating on a post contingency basis (i.e. not an "end-to-end" line loading issue). Therefore, this is an LDF allocation issue.
36 | Congestion on Kluge - Cyfair 138 kV Line | SSWCS8 CYFKL_76_1 KL 138 CYF 138 (08/10/10) | 21 | 2010-08-13 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Houston Load Zone (HLZ) to Houston Hub spreads. | ? | Active | ? | [LUME 8/12/10] this constraint has occurred on 2 separate occasions between 8/11/10 and 8/12/10 and is typically associated with very high shadow prices (e.g. >$16,000). When this constraint is active, Houston Load Zone blows out over Houston Hub. [ERCOT 8/12/2010]The line from Kluge to Cyfair is binding at its limit ( around 290MW) for peak hours under contingency SSWCS8: The shfit factor is only their to this constraint from LZ_HOUSTON and is around -2% Contingency SSWCS8 definition is to outage quite a few lines and breakers. In the post-contingency network, this line KL 138.0 CYF 138.0 becomes a radial line that feeds CYF_TR1, GE_TR1, GE_TR2, SA_TR7, and SA_TR8. So once again the energy only/PTP in LZ_HOUSTON is the only control variable with nozero shift factor for this constraint and the shift factor is simply sum of LDF of 5 loads. Correspondingly, LZ_HOUSTON is capped by this constraint and the shadow price on this constraint shot up. [CNP 8/18/2010] : The contingency indicated on the spreadsheet provided by Luminant indicates the contingency causing the loading on Kluge to Cyfair is the Crosby to Scenic Woods. This contingency should not result in significant change in the loading of Kluge-Cyfair and would not result in Kluge to CyFair being radial. ERCOT- CNP/Ebby John to work with ERCOT ops to look at radial/contingency interplay. Potential LDF issue.
37 | Congestion on ST. JO TU - SAINT JO 69 kV Line | BASE CASE | 21 | 2010-08-14 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting North Load Zone (NLZ) to North Hub spreads. | ? | Pending Closure - Radial Load Pockets | ? | [LUME 8/12/10] this constraint has occurred on 8 separate occasions between 6/11/10 and 8/12/10 (most recently on 8/11 and 8/12) and is typically associated with very high shadow prices (most recently on 8/12/10 >$516,000!). When this constraint is active, North Load Zone blows out over North Hub. [ERCOT 8/12/2010] This is a base case constraint from SNTJO to SAINT_JO. The line rating is 18MW. This line is a radial line that feeds four loads: These four loads are SAINT_JO_STJO___1, SAINT_JO_STJO___2, NOCONATN_NOCONA_2, and NOCONATN_NOCONA_1. The LDF are 1.031, 1.745, 4.088 and 3.510, respectively. Since it is a radial line in LZ_NORTH, only LZ_NORTH has shift factor -0.00079. Therefore, as well discussed before, LZ_NORTH is capped by this binding constraint and the line shadow price shot up. It seems that SAINT_JO_STJO___1 does not exist in current zonal production. However, its contribution is relatively small according to its LDF. [LUME 8/18/10] An "end-to-end" line loading assesment was performed in the SSWG 2010 Summer Planning case to determine whether overloads of this line seem to be a true irresolvable constraint from a physical perspective or a LDF issue in the way the DAM is allocating the load. In the SSWG case, loading of this line is only 50% of its rating on a post contingency basis (i.e. not an "end-to-end" line loading issue). Therefore, this is an LDF allocation issue. Dive mtg 8/19- Look at LDF or LoadRollover
38 | Congestion on Garrett - Midtown 138 kV Line | DGBY_GS8 GT_MID90_1 GT 138 MID 138 (08/10/10) | 21 | 2010-08-15 | LUME | Modeling | DAM | 1 | Severe congestion that is negatively impacting Houston Load Zone (HLZ) to Houston Hub spreads. | ? | Active | ? | [LUME 8/12/10] this constraint has occurred on 4 separate occasions between 8/5/10 and 8/12/10 and is typically associated with very high shadow prices (e.g. >$9,600). When this constraint is active, Houston Load Zone blows out over Houston Hub. [ERCOT 8/15/2010] DAM OD 08/11: At hour 12, its shadow price is 1400 $/MWh. This constraint is due to the contingency DGBY_GS8. It is a contnigency with outage elements from GBT to GABLE and from HARDY to CROKET. The rating in real time is via the telemetry and 311. However, the dynamic rating in DAM is 282 at hour 12. Assuming the given dynamic rating in DAM is correct, we have performed the sensitivity analysis and the dominant marginal resources are an Energy Only Bid at the Houston Load Zone whose shift factor is -0.002 and the generating units WAP_WAP_G1, WAP_WAP_G2, waP_WAP_G3 with shift factors of 0.04. [Dive mtg 8/17] - Confirmation of periodic real-time congestion, Wayne Kemper (Centerpoint) agreed to look at Garrett-to-Midtown since periodic in real-time, but chronic in DAM. [CNP 8/19 Update] - The contingencies, ratings and potential congestion seem appropriate. I notice that 13 of the 19 million in congestion shown on the spreadsheet provided by Luminant occurs on August 10th and there was no actual congestion on that date. So while the contingency and possible loading are reasonable, my guess is the generation dispatch was out of the ordinary and departed from the actual dispatch. Dive mtg 8/19- Look at LDF or LoadRollover
34 | LFC test 8/4/2010: putnam phase shifting transformer issue |  |  | 2010-08-05 | LUME |  |  | 2 |  | John Adams | Active |  | [LUME 8/18/10] How is ERCOT modeling the tap settings of this phase shifting transformer (PST) and all of the others in the system on both a DAM and RTM market basis? What steps are being taken to capture the full system benefit of these flexible AC transmission system devices? Dive 8/19 ERCOT pulls from generic constraint limit calculation (looking at COPs and LDF). Looking to improve 3-day ahead generic constraint study. Fixed PST/TapPosition for entire day, cannot change hourly (DAM not possible with CRR, RUC consider change after go-live- but original design did not have phase shifters on system- back in 2007) DEEP DIVE IA- ERCOT provide procedure summary of setting PST, consider exclude list - Determine process for adjusting tap setting off of neutral position - Opportunity to monitor-only transmission elements - Opportunity to set hourly in software (post go-live) - Algorithm to optimize tap settings within solution (post go-live) - noted that based on work with vendor changes to DAM much more complex than RUC (DAM may be impossible with interplay of CRR Offers/Options). [ERCOT 9/2] - CRR auction with Phase Shifter- Confirmed Phase Shifting transformers in model and used by CRR Auction, Tap setting used as modeled.
3 | Austrop 345/138 kV Auto Overloads |  |  | 2010-06-11 | LUME | SPS | DAM | 3 | Austrop autos overloading for the contingency loss of the other Austrop 345/138 kV Auto. Is Austrop SPS is not adequate enough to protect the Auto’s? Is this SPS being modeled in the DAM solution? | sai | Pending Software Update | Perhaps this has already been resolved since this constraint hasn't bound since 7/1/10. | Please close the loop with summitter on whether this issue has been resolved [LUME 8/10/10] suggest moving to Priority 3 until we see what happens when the vendor SPS solution is uploaded. What date does ERCOT expect that to occur? [ERCOT 8/10/2010] Software fix being deliverd 8/16. NPROD migration begining of September after testing.
4 | SPS ¦ Elkton - Athens 138 kV Overloads |  |  | 2010-06-11 | LUME | SPS | DAM | 3 | Elkton – Athens 138 kV line overloading for the contingency loss of Trinidad – Stryker Creek & Trinidad – Mt. Enterprise 345 kV double circuit in DAM results. Does this mean that the SPS is not adequate enough to protect the Elkton – Athens – Forest Grove 138 kV line? Is this SPS being modeled in the DAM Solution? | sai | Pending Software Update | ? | Initially ERCOT believed that the the trigger point for the Elkton SPS had not been modeled correctly in the DAM (157MVA vs. 114MVA) and that the issue was going to be corrected in the DSV20 load on 7/26/10; however, this issue remains even for DAM results up through 7/30/10 [ERCOT 8/6/2010] The reason why this showed up again is due to the second issue with SPS - software issue - fixed in MMS5 P9 - tested DAM OD 7/28 at vendor site and verfied that SPS triggering issue is fixed and there are two contingencies (previous names DENTSC5 and DTRSENT5) for which SPS is properluy triggered and no constraints are generated. [LUME 8/10/10] suggest moving to Priority 3 until we see what happens when the vendor SPS solution is uploaded. What date is that expected to occur? [ERCOT 8/10/2010] Software fix being deliverd 8/16. NPROD migration begining of septmeber after testing.
18 | Congestion on North Carbide - Port Lavaca 69 kV line |  |  | 2010-07-29 | LUME | Modeling | DAM | 3 | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/29/10 NATF presentation for more detail) | ? | Active - Monitoring | ? | [ERCOT 8/5/2010] This constraint does not contribute significantly to the SPP difference between south Load zone and south hub.This is a binding constraint due to contingency SLOLBLE8 . The contigency defition of SLOBLBE8 is to outage the line BLESSI_LOLITA1_1 from LOLITA to BLESSING. The binding constraint is at the line from NCARBIDE to PV_TAP at its limit of 61MW. At hour 17, its base case flow is 48MW. The base case flow of the outaged line from LOLITA to BLESSING is 152MW at hour 17. The key driver of this post-contingency flow include a number of large CC unit such as VICTORIA, LGE, INGLCO, NUE, CCEC, DUKE, etc, and a number of large PTP sources at these CC unit settlement points. The only resources that have effective negative shift factors are the small unit RAYBURN G1, G2, and G3 ( the shift factor is -0.048). Their HSL total is around 50MW. However, G1 and G2 are AS only and G3 is disconnected. With the binding constraint with expensive shadow price, such settlement point with positive shfit factor as FORMOSA and LGE have lower LMP and such settlement point with negative shfit factor such as RAYBURN and STP have higher LMP.
47 | DAM 08/05: Contingency SSIGSAN8 causing overload from KenedySW to Kenedy - 69 KV (KENEDS_KENEDY1_1) for all 24 hours. Highest shadow price of $27000 set for hour 14. |  | 21 | 2010-08-05 | ERCOT |  | DAM |  | [ERCOT 8/10/2010] This contingency outages 138 KV line from SANMIGL to SIGMOR. The overloaded line at 69 KV from kenedysw to kenedy is rated at 38 MW. The high shadow price at HE 14 is due to marginal CRR offers from CALAVERs to LZ_CPS. The shift factor difference between LZ_CPS and CALAVERS is positive and DAM buys back capacity. |  | Pending Closure |  | [ERCOT 8/10/2010] This contingency outages 138 KV line from SANMIGL to SIGMOR. The overloaded line at 69 KV from kenedysw to kenedy is rated at 38 MW. The high shadow price at HE 14 is due to marginal CRR offers from CALAVERs to LZ_CPS. The shift factor difference between LZ_CPS and CALAVERS is positive and DAM buys back capacity.
41 | Potential wrong line rating on Long Creek - Abilene Mulberry Creek 345 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 942 MVA, 2 Hour = 956 MVA ERCOT Nodal DSV 21, Continuous = 942 MVA, 2 Hour = 956 MVA ERCOT SSWG 2010 Sum 1, Continuous = 1072 MVA, 2 Hour = 1072 MVA | ? | Pending Closure DSV24 | ? | [LUME 8/13/10] This line belongs to Oncor. The 956 MVA rating in the Zonal Ops and Nodal DSV 21 case appear to be 1,600 amp terminal equipment limitations, whereas the 1072 MVA rating from the SSWG planning case is Oncor's standard conductor rating for bundled 795 kcmil 345 kV lines. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
42 | Potential wrong line rating on Cleburne - Air Liquid 138 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line beween the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuos = 350 MVA, 2 Hour = 350 MVA ERCOT Nodal DSV 21, Continuos = 350 MVA, 2 Hour = 350 MVA ERCOT SSWG 2010 Sum 1, Continuos = 428 MVA, 2 Hour = 428 MVA | ? | Pending Closure DSV24 | ? | [LUME 8/13/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
43 | Potential wrong line rating on Big Spring - Airpark 138 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line beween the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuos = 84 MVA, 2 Hour = 84 MVA ERCOT Nodal DSV 21, Continuos = 86 MVA, 2 Hour = 86 MVA ERCOT SSWG 2010 Sum 1, Continuos = 124 MVA, 2 Hour = 124 MVA | ? | Pending Closure DSV24 | ? | [LUME 8/13/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files. [LUME 8/18/10] Larry Reiter (Oncor - Planning) confirmed with Luminant that the SSWG rating of 124 MVA is the correct rating. Luminant has requested that David Bogen with Oncor submit a NOMCR to correct the Zonal and Nodal Operations ratings [ERCOT] - NOMCR submitted to fix- will be in DSV 24
45 | Potential wrong line rating on Cedar Creek - Cedar Creek PU 138 kV line |  |  | 2010-08-13 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line beween the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuos = 251 MVA, 2 Hour = 251 MVA ERCOT Nodal DSV 21, Continuos = 252.6 MVA, 2 Hour = 252.6 MVA ERCOT SSWG 2010 Sum 1, Continuos = 124 MVA, 2 Hour = 124 MVA | ? | Pending Closure DSV24 | ? | [LUME 8/13/10] This line belongs to Oncor. We aren't concerned about the 1 to 2 MVA difference between the Zonal and Nodal Ops case; however, the difference between the 251 MVA rating in Zonal Ops and the 124 MVA SSWG planning case is material. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files. [LUME 8/18/10] Larry Reiter (Oncor - Planning) confirmed with Luminant that the SSWG rating of 124 MVA is the correct rating. Luminant has requested that David Bogen with Oncor submit a NOMCR to correct the Zonal and Nodal Operations ratings [ERCOT 8/24] - Confirmed NOMCR submitted to fix- will be in DSV 24
50 | Potential wrong line rating on Big Brown E - Venus N 345 kV line |  |  | 2010-08-18 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 956 MVA, 2 Hour = 956 MVA ERCOT Nodal DSV 21, Continuous = 976.9 MVA, 2 Hour = 976.9 MVA ERCOT SSWG 2010 Sum 1, Continuous = 1072 MVA, 2 Hour = 1072 MVA | ? | Pending Closure DSV24 | ? | [LUME 8/18/10] This line belongs to Oncor. Minor difference between the Zonal Ops and Nodal DSV21 case, appears to be minor temperature variations for dynamically rated line and aren't a concern here. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files. [ERCOT 8/26] - Confirmed NOMCR submitted to fix- will be in DSV 24
53 | Potential wrong line rating on Garden City - Chalk 69 kV line |  |  | 2010-08-18 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 24 MVA, 2 Hour = 24 MVA ERCOT Nodal DSV 21, Continuous = 24 MVA, 2 Hour = 24 MVA ERCOT SSWG 2010 Sum 1, Continuous = 42 MVA, 2 Hour = 42 MVA | ? | Pending Closure DSV24 | ? | [LUME 8/18/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files. [ERCOT] - Confirmed NOMCR submitted to fix- will be in DSV 24
55 | Potential wrong line rating on Key - Lamesa 138 kV line |  |  | 2010-08-18 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 143 MVA, 2 Hour = 143 MVA ERCOT Nodal DSV 21, Continuous = 146 MVA, 2 Hour = 146 MVA ERCOT SSWG 2010 Sum 1, Continuous = 186 MVA, 2 Hour = 186 MVA | ? | Pending Closure DSV24 | ? | [LUME 8/18/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files. - [ERCOT 8/26 ] - NOMCR submitted to fix- will be in DSV 24
58 | Potential wrong line rating on Permian - Wickett 69 kV line |  |  | 2010-08-18 | LUME | Ratings Error | DAM | 1 | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 60 MVA, 2 Hour = 60 MVA ERCOT Nodal DSV 21, Continuous = 63.34 MVA, 2 Hour = 63.34 MVA ERCOT SSWG 2010 Sum 1, Continuous = 80 MVA, 2 Hour = 80 MVA | ? | Pending Closure DSV24 | ? | [LUME 8/18/10] This line belongs to TNMP. LUME sent an email to Mohammed Uddin at TNMP to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files. [LUME 8/24/10] TNMP reports that the correct rating for this line is 72 MVA (600 A CT limitation) and that NOMCR 6876-1 has been submitted to correct it, as well as, an IDEV will be submitted to correct the SSWG rating. TNMP says that Oncor will need to submit a NOMCR to change the rating on their terminal and owner share.
DSV22= Aug 18
DSV 23 = Sep 1
DSV24 = Sep 15

## Contingency Issues
Status | Contingency | DAM Issue # | Issue Description | Comments | Temporarily disabled/fixed in EMS | Temporarily disabled/fixed in MMS | Temporary fix verified 'as of' date * | Target DSV Resolved
Closed- removed in DSV23 | DFORFRN5 | 22 | Invalid contingency; need NOMCR to remove from NMMS | Planning submitted a NOMCR: In-service date 8/14/10 | N/A | N/A | N/A | DSV23
Closed- removed in DSV23 | DELKMLS5 | 22 | Bad contingency definition; need NOMCR to remove from NMMS | Replaced by DTRCELK5 | N/A | N/A | 2010-09-01 | DSV23
Closed- active in DSV23 | DTRCELK5 | 22 | New contingency created to replace DELKMLS5; need to add in NMMS | New contingency to replace DTRCELK5; Planning submitted a NOMCR: In-service date 8/14/10 | N/A | N/A | 2010-09-01 | DSV23
DSV24 | SAMGJEW8 | 35 | Single Circuit, requires special modeling in NMMS to include additional definition elements | Planning submitted a NOMCR: In-service date 8/14/10 to include opening of autotransformer as part of the definition. | Yes | Yes | 2010-09-01 | DSV24
Closed- corrected/active DSV23 | SSD5SND8 | N/A | Invalid contingency; zBR versus a real line; need NOMCR to correct in NMMS | Planning submitted a NOMCR: In-service date 9/1/10 to correct Model | N/A | N/A | 2010-09-01 | DSV23
Closed- removed in DSV23 | SSD5SD28 | N/A | Bad contingency definition, fixed in EMS | De-Actived Contingency is EMS and DAM has been removed in DSV23 | N/A | N/A | 2010-09-01 | DSV23
* Note: Statuses confirmed by DA Operator & IT Support on 8/13/2010
Notes from Chad Thompson
Line/ZBR | DSV 22 Contingency | DSV 23 Contingency | Comments
SD5SES_SDSES_1 (ZBR) | SSD5SD28 | SSD5SDS8 | Now defined as node-to-node; should not be in EMS or MMS with DSV 23
SD5SES_SDSES_2 (ZBR) | SSD5SD18 | SSD5SD28 | Now defined as node-to-node; should not be in EMS or MMS with DSV 23
Yes the contingency ID did change for this contingency
1726_A | SSD5SND8 | SSD5SND8 | Valid contingency in both cases- this is one of 3 small ac lines that connects the Luminant Sandow Yard to the Oncor Yard
1725_A | SSDSSN18 | SSDSSN28 | Valid contingency in both cases- this is the second of 3 small ac lines that connects the Luminant Sandow Yard to the Oncor Yard
1728_A | SSDSSN28 | SSDSSND8 | Valid contingency in both cases- this is the third of 3 small ac lines that connects the Luminant Sandow Yard to the Oncor Yard

## Line Rating Issues
Status | DAM Issue # | Line | Issue Description | Comments | Temporarily fixed in EMS | Temporarily fixed in MMS | Temporary fix verified 'as of' date * | Target DSV Resolved
Pending Model Load | 41 | Long Creek - Abilene Mulberry Creek 345kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | No | No |  | DSV24 NOMCR submitted 956/956/1100, DSV24
Pending Model Load | 42 | Cleburne - Air Liquid 138kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | Yes | Yes |  | DSV24 NOMCR 7807_1 effective 8/27/10 submitted 8/26/10
Pending Model Load | 43 | Big Spring - Airpark 138kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | Yes | Yes | 2010-08-25 | DSV 24 NOMCR submitted 124/124/127, DSV24
Pending Model Load | 45 | Cedar Creek - Cedar Creek PU 138kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | Yes | Yes | 2010-08-25 | DSV24 NOMCR submitted 124/124/127, DSV24
Pending Model Load | 50 | Big Brown E - Venus N 345 kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | Yes | Yes | 2010-08-25 | DSV24 NOMCR submitted 1052/1052
Pending Model Load | 53 | Garden City - Chalk 69 kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | Yes | Yes | 2010-08-25 | DSV24 NOMCR submitted 42/42/42
Pending Model Load | 55 | Key - Lamesa 138 kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | Yes | Yes | 2010-08-25 | DSV24 NOMCR submitted 186/186/196
Pending Model Load | 58 | Permian - Wickett 69 kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | NA | NA | NA | DSV24 NOMCR submitted - Deletion actions only of DAMPs (dynamic amp ratings), line remains rated at 72/72/72 MVA
Resolved | 51 | Bosque generation step up xfmrs | Potential Ratings and Impedance Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to LCRA to research and correct with NOMCR |  |  |  | Fixed DSV23
Pending feedback / NOMCR | 52 | Elkton - Forney 345 kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR |  |  |  | Fixed- DSV23 fixed 956/956/1100 MCR 7430_4
Resolved | 21 | Decartur Tap - Rhome 138 kV | DAM congestion negatively impacting solution Ratings Error, need to update Model | Line rating of 124, needs to be updated to 186 MVA. Pending NOMCR submission |  |  |  | Fixed DSV 23
Resolved | 6 | Hutto - Round Rock NE 138 kV | DAM line bound hourly Ratings Error, need to update Model | Line rating of 237, needs to be updated to 326 MVA normal rating. NOMCR submitted w/ Ratings 326/326/368 | NA | NA | NA | NOMCR submitted Corrected in DSV22
Resolved | 20 | Bennett Rd. - Decartur Tap 138 kV | DAM congestion negatively impacting solution Ratings Error, NOMCR submitted 7/29/10 | Line rating of 124, needs to be updated to 186 MVA. NOMCR submitted 7/29 w/ Ratings 214/214/229. | NA | NA | NA | Corrected in DSV22
Resolved | 33 | Wise County - Bridgeport 138 kV | DAM congestion negatively impacting solution Ratings Error, need to update Model | Line rating of ~200, needs to be updated to 388 MVA. Brazos submitted NOMCR 7/21 | NA | NA | NA | Corrected in DSV22
Resolved | 1 | Deepwater - Applied Energy 138kV | DAM Binding Shadow Price Report Ratings Error, need to update Model | Line rating of 48 MVA, may need to be updated to match SSWG case 180/191/220 MVA (Normal/2 hr/ 15 min). | NA | NA | NA | Verified correct by CNP, to remain rated at 48/48/48 MVA
Resolved | 2 | West - North Dynamic Stability Limit | RT Ratings 2-3X higher than DAM Binding reports Ratings Error, need to update Model | Line rating of ?? MVA, manually updated to 2400 MVA | NA | NA | NA | Corrected in DSV21
Resolved | 26 | Numerous line ratings inconsistent | Comparison List Various line ratings inconsistent |  |  |  |  | Numerous rating given indiv issue list
Resolved | 44 | Buda - Rutherford 138kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to LCRA to research and correct with NOMCR | NA | NA | NA | LCRA confirmed Nodal DSV21 model is correct & SSWG model was wrong - ready to close
Resolved | 49 | Big Brown W - Venus S 345 kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | NA | NA | NA | Line ratings verified and no changes to line rating 956/956/1100
Resolved | 54 | Gilleland - McNeil 138 kV | Potential Ratings and Impedance Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | NA | NA | NA | Per LUME this is no longer an issue
Resolved | 56 | Marion - Skyline 345 kV | Potential Ratings Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | NA | NA | NA | Nodal/Zonal/SSWG models are consistent 8/31/2010; no action required. 1076MW
Resolved | 57 | Oran - Morris Sheppard 69 kV | Potential Ratings and Impedance Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | NA | NA | NA | Planning values to be changed
Resolved | 59 | Turnersville - Buda 138 kV | Potential Ratings and Impedance Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | NA | NA | NA | Planning values to be changed
Resolved | 60 | MEC Plainview - Snyder 138 kV | Potential Ratings and Impedance Error | Inconsistencies across Nodal/Zonal/SSWG LUME sent email to Oncor to research and correct with NOMCR | NA | NA | NA | Values aligned as of 8/31

## Model Issue Tracking
Status | DAM Issue # | Issue Description | Comments | Resolved
| 15 | Congestion on Trinidad - Winkler 138 kV line Severe congestion that is negatively impacting North Load Zone (NLZ) to North Hub spreads | Change Load to be zero in RARF- issues still to discuss versus systemic (psuedo measurement for SE)
Closed | 30 | Congestion on Applied Energy (APD_ST1) Severe congestion that is negatively impacting Houston Load Zone (HLZ) to Houston Hub spreads. | Changed to Non Conform Load and updated the load schedule. Submitted as part of the latest RARF update to the station which will be energized on 8/16 and will be in DSV23 (Scheduled NPROD date of 9/1/2010). | DSV23
Closed | 31 | DAM OD 8/4/2010: Generic constraint for import into DFW is incorrect in DSV 21 | Correction is expected to become effective in DSV23 (Scheduled NPROD date of 9/1/2010). | DSV23

## Closed
Issue # | Issue Title | Date Submitted | Submitter | Category | Mkt. | Priority | Issue Description | Assigned To | Status | Estimated Resolution Date | Comments
7 | Contingency Definition Report | 2010-08-02 | LUME | Reports | DAM | 1 | The Contingency Definition Report Provided on 8/1/2010 by Alan Adams, doesn't contain all the contingency names. Problems with DSV20, DSV21 |  | Closed |  | Additionally, it needs to contain the contingency definitions (i.e. what branches are outaged) for each of the contingency defintions. 8/5/2010 - new report for DSV 20 and DSV 21 will be created by NMMS. Need to figure out how this will be posted. The contingency names will be consistent from DSV 22 ONWARDS [LUME 8/12/10] - this issue was closed at the 8/10/10 conf. call, as all the necessary reports for DSV 20 and 21 had been delivered on 8/6/10. Thanks!
23 | Congestion on S.E. Nacogdoches 345/138 kV auto | 2010-07-29 | LUME | Modeling | DAM | 3 | Congestion on this auto appears to be legitimate (see 7/29/10 NATF presentation for more detail) |  | Closed |  | This congestion should be elimiated soon by SPS #21 that Oncor is installing during the Fall of 2010 [LUME 8/10/10] Suggest moving to Priority 3 and monitor the impact of the upcoming SPS #21 installation [LUME 8/12/10] Suggest moving to Closed status given that Oncor will be installing SPS #21 in the Fall of 2010
26 | Potential wrong line rating on BTE_AT-1 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on BTE_AT-2 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on BUFF_GAP_C1 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on BUFF_GAP_C2 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on BUFF_GAP_FMR2 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Calveras - Pawnee 345 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on CHE_SUT1 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on CHE_SUT4 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Coleto Creek - Victoria 138 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on CCEC_CTG1 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Elgin - Gilleland 138 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Elm Creek - Hill Country 345 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Holly - Brackenridge 69 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Krum - Krum Tap 138 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on LARDVFT_VFTN | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on LARDVFT_VFTS | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on LEG_MT1 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Lobo - Laredo VFT North | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on PSG_XT2 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on PSG_XT3 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on PSA_TR1 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Roanoke Sw. - Elizabeth Creek 138 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Sharon Ridge Exxon - Bluff Creek Sw. 138 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on Silver City - Barclay 69 kV line | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on SWEETWN4_5 | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
26 | Potential wrong line rating on WHCCS_1HX | 2010-06-25 | LUME | Ratings Error | DAM | 1 | Ratings between Nodal Ops and SSWG Case Don't Match |  | Closed |  | As of the DSV21 Nodal Case (implemented 8/4/10) - issue was corrected
6 | Hutto - Round Rock NE 138 kV Line Rating | DAUSGAR5 1660__C HUTTO 138 RRNES 138 (07/31/10), DHUTGIL8 1660__C HUTTO 138 RRNES 138 (08/10/10) | 21 | 2010-07-30 | LUME | Ratings Error | In the DAM results for 7/31/10, the Hutto – Round Rock NE 138 kV Line bound every hour of the day with a reported line rating of 237 MVA (likely a dynamic line rating). Both the SSWG planning case for summer 2010 and the ERCOT Transmission Project Information Tracking (TPIT) database indicate that this line was just rebuilt in June 2010 for 326 MVA nominal rating. | 1 | Closed | John Adams | LUME believes that this may be an issue where the Nodal Operations model has not been updated and is still showing the old line rating. Please research this, notify us of your findings, and update the model as appropriate. [ERCOT 8/5/2010] the current DSV where this will be corrected is DSV 24 [LUME 8/10/10] why shouldn't this incorrect line rating be fixed in EMS and all inflight NMMS model builds ASAP? [ERCOT 8/11/10] Ratings on line 1660_C from Hutto to Round Rock NE have been updated to 326/326/368. DSV 22-Aug18 [LUME 8/18/10] Constraints due to this incorrect line rating no longer show up starting with the 8/19/10 DAM results (indicating that ERCOT's correction in DSV22 that was loaded on 8/18/10 worked). Suggest moving to closed status on 8/19/10 conf. call.
19 | Congestion on Odessa North - Odessa Basin 69 kV line | SPBSPB28 6915__A ODNTH 69 ODBSW 69 (07/31/10) |  | 2010-07-29 | LUME | Modeling | Severe congestion that is negatively impacting West Load Zone (WLZ) to West Hub spreads (see 7/29/10 NATF presentation for more detail) | 1 | Closed | ? | [ERCOT 8/5/2010] Bad contingency definition. This constraint is under contingency 'SPBSPB28', new from DSV 20. System operations confirmed the definition are not correct. This contingency has been excluded by both EMS and MMS since 8/3 [LUME 8/12/10] - this line last showed up in the DAM on 8/4/10 (i.e. one day after the fix outlined above was implemented). Please confirm that there is some reasonable explanation for its occurrence after the fix was in place. Perhaps the correction to the model occurred late on 8/3/10 after the 8/4/10 DAM was already complete. Just wanting to make sure that this issue has truly been corrected. [ERCOT 8/12/2010] SPB5PBS8 and SSD5SDS8 single circuit contingencies have been removed from the model in DSV 22 (Scheduled NPROD date of 8/18/2010). [LUME 8/18/10] Constraints due to this incorrect contingency no longer show up starting with the 8/19/10 DAM results (indicating that ERCOT's correction in DSV22 that was loaded on 8/18/10 worked). Suggest moving to closed status on 8/19/10 conf. call.
20 | Bennett Rd. - Decartur Tap 138 kV Line Rating | SJACREN8 910__D BNTSW 138 DCRTP 138 (07/30/10) |  | 2010-07-29 | LUME | Ratings Error | Congestion on this line seems to be negatively impacting Barton Chapel, Graham, Oklaunion, and WF Cogen (see 7/29/10 NATF presentation for more detail) | 1 | Closed | ? | Luminant Energy understands that Oncor has identified that the correct static rating for this line is 186 MVA rather than 124 MVA and will be filing a NOMCR to correct this. [ERCOT 8/5/2010] Additional analysis information. 1. This congestion are negatively impacting Barton Chapel Wind Farm, Graham, Oklaunion, and WF Cogen. 2. Th wind resource offer negative EOCs. 3. Resources EMSES_UNIT1, EMSES_UNIT2 and EMSES_UNIT3 with negative shift factors were not availble for DAM. [LUME 8/10/10] What is the update on getting the incorrect line rating fixed? [ERCOT 8/11/10] Ratings updated to 214/214/229. NOMCR submitted on 7/29/2010 with an Energization date of 8/7/2010. NOMCR included in DSV22 (Scheduled NPROD date of 8/18/2010). [LUME 8/18/10] Constraints due to this incorrect line rating no longer show up starting with the 8/19/10 DAM results (indicating that ERCOT's correction in DSV22 that was loaded on 8/18/10 worked). Suggest moving to closed status on 8/19/10 conf. call.
26 | Numerous Line Rating Questions (see separate tab) |  |  | Various | LUME | Ratings Error | Various lines that have shown up as overloaded elements during congestion have materially different ratings than either the Network Model or the Planning Model indicating that their may be a ratings error in one or more of these models that needs verified | 1 | Closed | ? | Details in Old_Rating_Issues tab [LUME 8/18/10] This list of ratings has been reviewed on 8/18/10 and all ratings that are now correct has been moved to the closed list and all ratings that are still incorrect have been entered as specific items in the master DAM Issues List (item numbers #49 - #60)
33 | Wise County - Bridgeport 138 kV Line Rating | SBLSJAC8 560_A_1 WISECNTY 138 BRGPR 138 (08/10/10) | 22 | 2010-08-05 | LUME | Ratings Error | Congestion on this line seems to be negatively impacting Jack County | 1 | Closed | sai | [LUME 8/12/10] This line rating should be 388 MVA nominally (per NOMCR submitted by Brazos on 7/21/10) and was previously modeled as ~200 MVA. During the 5 Hour LFC test on 7/21/10 this rating was corrected by Brazos with a NOMCR and ERCOT loaded it into the EMS without delay. Some how, the old lower line rating started showing up in DAM again on 8/5/10 and has continued to show up nearly every DAM since then. This needs corrected ASAP to match the Brazos NOMCR. [ERCOT 8/12/2010] Per ONCOR: This a BEPC owned line that id jointly operated with Oncor. The ratings on this line were updated during the last 24 hour LFC test. This rating information is correct (388/388/388). It was lower at the start of the last 24 hour test. (DSV 22- Aug18) [LUME 8/16/10] When will the updated 388/388/388 MVA ratings make in back into Nodal production? As late as the DAM for 8/17/10, this line continues to constrain with a rating of ~188 MVA. [LUME 8/18/10] Constraints due to this incorrect line rating no longer show up starting with the 8/19/10 DAM results (indicating that ERCOT's correction in DSV22 that was loaded on 8/18/10 worked). Suggest moving to closed status on 8/19/10 conf. call.
13 | Congestion on Pearsall 138/69 kV auto |  |  | 2010-07-19 | LUME | Modeling | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/19/10 NATF presentation for more detail). Possible cause - phase shifters, missing 345 KV line - san miguel - rio lobo? | 3 | Closed | sai | [ERCOT 8/6/2010] Analysis presented during the 8/5/10 Nodal DAM Deep Dive, indicates that remaining overloads are due to Rayburn generation not participating in the DAM [LUME 8/10/10] suggest moving to a priority 2 until we see some DAM results that includes virtual offers that LUME intends to submit to make up for the generation that is apparently not particiating in the market trials in this area. [LUME 8/12/10] suggest moving to a priority 3 based on initial results of 8/11 and 8/12 DAMs where LUME submitted virtual offers to make up for missing generation in the Valley that effects this constraint. If this behaves well over the next several DAMs, then we should look at closing it out. [LUME 8/18/10] Based on recent DAM outcomes since, invalid contingencies corrected, suggest closing on the 8/19/10 conf. call.
17 | Congestion on LaPalma - Villa Cavazos 138 kV line |  |  | 2010-07-29 | LUME | Modeling | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/29/10 NATF presentation for more detail) | 3 | Closed | sai/John Adams | [ERCOT 8/5/2010] Resources at SilasRay did not participate DAM. However, they were dispatched in Zonal real time. When SilasRay were not availble, DAM will reduce the generation from Duke, North Edinburg and curtail the clearing at LZ_SOUTH. 8/5/2010 John to ask PUB to participate in the DAM [ERCOT 8/12/2010]The most effective unit for solving this contingency constraint is: 'SILASRAY_SILAS_10' 'SILASRAY_SILAS_5' 'SILASRAY_SILAS_6' 'SILASRAY_SILAS_9' SILASRAY_SILAS_9 and SILASRAY_SILAS_6 consist of CC plant SILASRAY_CC1: SILASRAY_CC1_1 SILASRAY_SILAS_9 Primary CT SILASRAY_CC1_2 SILASRAY_SILAS_9 Primary CT SILASRAY_CC1_2 SILASRAY_SILAS_6 Primary ST All these four units have around -0.5 shfit factor. The sum of their HSL is about 100MW. However, none of them ( either regular unit and CC plant) participate in the 07/28 DAM MT ( no 3part offer at any hour). Without them, only CC units Duke, Frontera, and NE Edinbuurg have shift factor ( 0.0016, 0025843, 0.0015636 ) for this constraint. The LZ_SOUTH has around -0.04 shift factor for this constraint. Essentially, the units produced counter flow to balance the flow from LZ_SOUTH on this constraint. Since the unit shfit factor is much smaller, the LZ_SOUTH has to be curtailed to satisfy the constraint. [LUME 8/18/10] Based on the information provided by ERCOT on 8/12/10 and recently more well behaved congestion on this line since LUME started submitting offers at this site to offset the fact of PUB not submitting offers, suggest moving to closed on the 8/19/10 conf. call.
44 | Potential wrong line rating on Buda - Rutherford 138 kV line |  |  | 2010-08-13 | LUME | Ratings Error | A comparison of the line ratings of this line beween the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuos = 190 MVA, 2 Hour = 190 MVA ERCOT Nodal DSV 21, Continuos = 190 MVA, 2 Hour = 190 MVA ERCOT SSWG 2010 Sum 1, Continuos = 220.6 MVA, 2 Hour = 220.6 MVA | 1 | Closed | ? | [LUME 8/13/10] This line belongs to LCRA. LUME sent an email to Sergio Garza at LCRA to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files. [LUME 8/18/10] Brad Woods (LCRA - Planning) confirmed with Luminant that the ERCOT Zonal Operations and ERCOT Nodal DSV21 ratings are correct and that the SSWG rating will be corrected. He further pointed out that LCRA already has a project underway to upgrade this limiting terminal equipment by May 2011 as shown in ERCOT's TPIT report. Based on this information, which shows that the Nodal model is correct, Luminant recommends moving this issue to closed status after the 8/19/10 conf. call.
12 | Congestion on Derby - Pearsall 69 kV line |  |  | 2010-07-19 | LUME | Modeling | Severe congestion that is negatively impacting South Load Zone (SLZ) to South Hub spreads (see 7/19/10 NATF presentation for more detail). Possible cause - phase shifters, missing 345 KV line - san miguel - rio lobo? | 3 | Closed | sai | Between 5/4 & 7/15, bound 11 days in Nodal and 1 days in Zonal. ERCOT researched this and found that it was an incorrect contingency definition (reported at 7/29 NATF mtg). Issue still shows up in 7/31/10 DAM. When will Network model get corrected? [ERCOT 8/6/2010] As per ERCOT analysis presented at NATF- bad contingency definition SBATPEA8. Additionally, analysis presented during the 8/5/10 Nodal DAM Deep Dive, indicates that remaining overloads are due to Rayburn generation not participating in the DAM [LUME 8/10/10] suggest moving to a priority 2 until we see some DAM results that includes virtual offers that LUME intends to submit to make up for the generation that is apparently not particiating in the market trials in this area. [LUME 8/12/10] suggest moving to a priority 3 based on initial results of 8/11 and 8/12 DAMs where LUME submitted virtual offers to make up for missing generation in the Valley that effects this constraint. If this behaves well over the next several DAMs, then we should look at closing it out. [LUME 8/18/10] Based on recent DAM outcomes since, invalid contingencies corrected, suggest closing on the 8/19/10 conf. call.
54 | Potential wrong line rating on Gilleland - McNeil 138 kV line |  |  | 2010-08-18 | LUME | Ratings Error | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 221 MVA, 2 Hour = 221 MVA ERCOT Nodal DSV 21, Continuous = 230.82 MVA, 2 Hour = 230.82 MVA ERCOT SSWG 2010 Sum 1, Continuous = 493 MVA, 2 Hour = 493 MVA Additionally, the line impedances were different as well, with the Zonal Ops and Nodal DSV21 case having an R, X, & B of: .00310 pu, .02906 pu, .00866 pu. The SSWG case has an R, X, & B of: .00286 pu, .02850 pu, .00869 pu | ? | Closed | ? | [LUME 8/18/10] This line belongs to LCRA. LUME sent an email to Sergio Garcia at LCRA to request that they figure out which ratings and impedances are correct and then submit model changes to correct the appropriate files. [LUME 8/24/10] LCRA reports "An MLSE limits the rating of the Gilleland - McNeil 138 kV line from its full conductor rating of 493 MVA. We are currently working to remove this MLSE. The SSWG case planning ratings do not show the temporary MLSE rating. The impedance for this line in the SSWG cases will be updated with the as-built information (R, X, & B: .00310 pu, .02906 pu, .00866 pu)."
24 | Congestion on Wolf Hollow - Rocky Creek 345 kV line | S_2127 152__A WOFHO 345 RKCRK 345 (07/10/10) |  | 2010-07-29 | LUME | Modeling | Congestion on this line seems to be negatively impacting Comanche Peak and Wolf Hollow (see 7/29/10 NATF presentation for more detail) | ? | Closed | ? | The contigency S_2063 is a single line outage between CPSES and PKRSW [LUME 8/12/10] - This line has constrained 11 different time between 7/27/10 and 8/12/10 (10 different DAM days - sometimes for multiple contingencies in a day). The two contingencies associated with this overload have been Comanche Peak - Parker (S_2063) and Comanche Peak - Johnson Sw. (S_2127). What is seems especially confusing about these constraint pairs being binding, is that all of our offline studies show substantial amounts of spare export margin (~650 MW to 780 MW) from Comanche Peak for these two contingencies when associated with overloads of Wolf Hollow - Rocky Creek. In our offline planning studies the Contingency outage of the Comanche Peak - Decordova 345 kV line associated with overloads of Wolf Hollow - Rocky Creek indicate that the export margin from Comanche Peak is only ~50 MW (i.e. much more constraining than the two constraints listed above); however, this overload pair hasn't yet shown up in the Nodal DAM. [ERCOT 8/12/2010] DAM OD 7/28: The base case flow on this outage line is 848MW at hour 17. The base case flow on the line from WOFOH ( Wolf Hollow) to RKCRK (Rocky Creek) is 818MW. The redispatch is binding the line constraint from WOFOH to RKCRK: The dominant drivers of the flow are: 1. A large PTP source at the settlement point CPSES_UNIT1 with 1216MW and another large PTP source at the settlement point CPSES_UNIT2. They are two expensive PTP bid at 500$ and they are all fully loaded. Represent the outputs of the two large nuclear units CPSES_UNIT1 and CPSES_UNIT2 ?. These two units do not participate the DAM. The shfit factor for these two units are 0.393. 2. The CC plant WHCCS_CT1 at configuation WHCCS_CC1_2. Its mw schedule is 369MW and its shift factor is 0.47 3. The CC plant TEN_CC1 at configuration TEN_CC1_1. Its mw schedule is 196 MW and its shfit factor is 0.1. Comanche Peak & Wolf Hollow are located at the sending end of the binding constraint with shadow price of 90$ at hour 17. Since CPSES and WOFOH have significant postive shift factor, their LMP will be brought down by this shadow price. [LUME 8/16/10] ERCOT's technical description on 8/12/10 of what is happening in the DAM regarding the primary units that have a loading impact on this constraint all make sense from a shift factor perspective; however, what doesn't make sense is why Wolf Hollow - Rocky Creek is constraining associated with the SCPSPKR5 and SJONCPS5 contingencies in the first place rather than the SDCSCPS5 (Comanche Peak - Decordova 345 kV line) contingencies. A deep dive by LUME into the PSS/E cases prepared by Sia Moorty for 8/4/10, reveal that the Comanche Peak - Decordova 345 kV line is effectively missing from the case (i.e. their is a radial 345 kV line from Comanche Peak - Decordova that doesn't connect to anything at Decordova). This missing line appears to be the root cause of the unexplained Wolf Hollow - Rocky Creek 345 kV line congestion. [Deep Dive Mtg 8/17] - Continue research with Oncor and Resource Entity, and after confirming issue determine whether there is quality check to prevent errors. [LUME 8/18/10] Constraints due to the Comanche Peak - Decordova 345 kV line being incorrectly modeled as open in DSV21 no longer show up starting with the 8/19/10 DAM results (indicating that ERCOT's correction in DSV22 that was loaded on 8/18/10 worked). Suggest moving to closed status only after ERCOT reports on what the root cause of the original modeling error was and what steps have been taken to mitigate it going forward. [ERCOT 8/24] The data came in correctly in the RARF. There was a data entry error while converting the RARF to a NOMCR. ERCOT’s data quality checks caught the error and sent a correction notice (status was not changed in Zonal). The breakdown occurred when an individual failed to follow through on the correction. We reviewed the training and went over the correction with that individual to prevent the problem in the future. In production, there are at least six different processes that could have potentially caught this error that are not being implemented for Market Trials because of the compressed time frame in which the DSVs are being delivered.
27 | NOIE CRR Offers restricted only to PCRRs? |  |  | 2010-08-05 | ERCOT |  | There is a need to confirm whether a NOIE can submit a CRR Offer against ANY CRR Option they own into the DAM | Reedy | Closed |  | Duplicate of issue 28
1 | Deepwater - Applied Energy 138 kV line rating | 23 | 2010-06-15 | LUME | Ratings Error | DAM | Is line rating correct? Shadow Price for the 138 kV line at its max was $13,149 (HE 16:00) and ave $6,618 for the Peak hours. The DAM Binding Shadow Price report indicates that line is rated at 48 MVA; however, the Summer 2010 SSWG case has the same line rated at 180/ 191/ 220 MVA (Normal/2 hr/15min MVA). | sai | Closed | Likely already resolved since this constraint hasn't bound since 7/17/10. | Please close the loop with summitter on whether this issue has been resolved [ERCOT 8/11/2010] ERCOT has contacted CNP about the rating on the line APDDW-2 coming out of the APD substation, and they have forwarded it the appropriate people in their company. A reply is expected by the end of the week. According to Centerpoint the 48 MVA rating on this line is correct and matches the SSWG case. I agree with Centerpoint that it is more than likely the 1 MW battery that could be causing problems here. A RARF was submitted recently to change the breaker status and expected load values at this station and a NOMCR has been submitted to make these changes with an energization date of 8/16. Hopefully these changes should correct any issues
2 | West - North Dynamic Stability limit |  | 2010-06-16 | LUME | Ratings Error | DAM | The limits being reported in Real Time are 2 – 3 times higher than the limits being reported in the DAM binding reports. How is the West – North Dynamic stability limit being modeled in the DAM? | sai | Closed | 2010-08-02 | This has been manually corrected. The last model load has the lower rating, but it was manually overridden in MMS. Corrected in DSV21 (2,400) [LUME 8/10/10] what rating for the West - North Stability Limit does ERCOT plan to utilize in the DAM model?
49 | Potential wrong line rating on Big Brown W - Venus S 345 kV line |  | 2010-08-18 | LUME | Ratings Error | DAM | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 956 MVA, 2 Hour = 956 MVA ERCOT Nodal DSV 21, Continuous = 956 MVA, 2 Hour = 956 MVA ERCOT SSWG 2010 Sum 1, Continuous = 1072 MVA, 2 Hour = 1072 MVA | ? | Closed |  | [LUME 8/18/10] This line belongs to Oncor. Minor difference between the Zonal Ops and Nodal DSV21 case, appears to be minor temperature variations for dynamically rated line and aren't a concern here. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
56 | Potential wrong line rating on Marion - Skyline 345 kV line |  | 2010-08-18 | LUME | Ratings Error | DAM | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 1076 MVA, 2 Hour = 1076 MVA ERCOT Nodal DSV 21, Continuous = 956 MVA, 2 Hour = 956 MVA ERCOT SSWG 2010 Sum 1, Continuous = 1076 MVA, 2 Hour = 1076 MVA | ? | Closed |  | [LUME 8/18/10] This line belongs to CPS. LUME sent an email to Basileo Rocha at CPS to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files [LUME 8/24/10] CPS Energy reports that the correct rating for this line is 1076 MVA and that a NOMCR has been submitted to correct this rating. [ERCOT AI- confirmed 1076 in current DSV]
57 | Potential wrong line rating on Oran - Morris Sheppard 69 kV line |  | 2010-08-18 | LUME | Ratings Error | DAM | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 23 MVA, 2 Hour = 23 MVA ERCOT Nodal DSV 21, Continuous = 22.9 MVA, 2 Hour = 22.9 MVA ERCOT SSWG 2010 Sum 1, Continuous = 194 MVA, 2 Hour = 194 MVA Additionally, the line impedances were different as well, with the Zonal Ops and Nodal DSV21 case having an R, X, & B of: .19300 pu, .32100 pu, .00520 pu. The SSWG case has an R, X, & B of: .04190 pu, .29190 pu, .00540 pu | ? | Closed |  | [LUME 8/18/10] This line belongs to Brazos. LUME sent an email to Dave Albers at Brazos to request that they figure out which ratings and impedances are correct and then submit model changes to correct the appropriate files.
59 | Potential wrong line rating on Turnersville - Buda 138 kV line |  | 2010-08-18 | LUME | Ratings Error | DAM | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 287 MVA, 2 Hour = 287 MVA ERCOT Nodal DSV 21, Continuous = 287 MVA, 2 Hour = 287 MVA ERCOT SSWG 2010 Sum 1, Continuous = 439.32 MVA, 2 Hour = 439.32 MVA Additionally, the line impedances were different as well, with the Zonal Ops and Nodal DSV21 case having an R, X, & B of: .00111 pu, .00790 pu, .01006 pu. The SSWG case has an R, X, & B of: .00150 pu, .00840 pu, .00964 pu | ? | Closed |  | [LUME 8/18/10] This line belongs to LCRA. LUME sent an email to Sergio Garcia at LCRA to request that they figure out which ratings and impedances are correct and then submit model changes to correct the appropriate files.
60 | Potential wrong line rating on MEC Plainview - Snyder 138 kV line |  | 2010-08-18 | LUME | Ratings Error | DAM | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 59 MVA, 2 Hour = 59 MVA ERCOT Nodal DSV 21, Continuous = 63 MVA, 2 Hour = 63 MVA ERCOT SSWG 2010 Sum 1, Continuous = 85 MVA, 2 Hour = 123 MVA Additionally, the line impedances were different as well (R, X, & B respectively): ERCOT Zonal Operations - .00789 pu, .02129 pu, .00120 pu ERCOT Nodal DSV 21 - .00001 pu, .00050 pu, .00000 pu ERCOT SSWG 2010 Sum 1 - .02328 pu, .08332 pu, .00134 pu | ? | Closed |  | [LUME 8/18/10] This line belongs to AEP. LUME sent an email to Paul Hassink at AEP to request that they figure out which ratings and impedances are correct and then submit model changes to correct the appropriate files.
61 | CPS PSEE Question | [7 empty] | Closed |  | Specifics to be sent to ERCOT regarding a PSSe question by CPS, ask ERCOT to share issue and response when details are available. [ERCOT 8/31]- Confirmation from CPS this is not an issue
21 | Decartur Tap - Rhome 138 kV Line Rating |  | 2010-07-29 | LUME | Ratings Error | DAM | Congestion on this line seems to be negatively impacting Barton Chapel, Graham, Oklaunion, and WF Cogen (see 7/29/10 NATF presentation for more detail) |  | Fixed with DSV 23 |  | Luminant Energy understands that Oncor has identified that the correct static rating for this line is 186 MVA rather than 124 MVA and will be filing a NOMCR to correct this. [ERCOT 8/5/2010] Additional analysis information. 1. This congestion are negatively impacting Barton Chapel Wind Farm, Graham, Oklaunion, and WF Cogen. 2. Th wind resource offer negative EOCs. 3. Resources EMSES_UNIT1, EMSES_UNIT2 and EMSES_UNIT3 with negative shift factors were not availble for DAM. [LUME 8/10/10] What is the update on getting the incorrect line rating fixed? [ERCOT 8/12/2010] ERCOT has not yet received a NOMCR from ONCOR to correct these ratings. Sent an email to ONCOR requesting them to provide an update.
51 | Potential wrong branch ratings and impedances for Bosque generation step up xfmrs |  | 2010-08-18 | LUME | Ratings Error | DAM | A comparison of the branch ratings and impedances of the five generator step up xfmrs at Bosque between the Nodal DSV 21 case and the SSWG 2010 Sum 1 case has shown material differences between the two for these five xfmrs. |  | Fixed with DSV 23 |  | [LUME 8/18/10] These five generation step up xfmrs are modeled by Brazos. LUME sent an email to Dave Albers at Brazos to request that they figure out which ratings and impedances are correct and then submit model changes to correct the appropriate files.
52 | Potential wrong line rating on Elkton - Forney 345 kV line |  | 2010-08-18 | LUME | Ratings Error | DAM | A comparison of the line ratings of this line between the Nodal DSV 21 case, the ERCOT Zonal Operations Case (8/2/10), and the SSWG 2010 Sum 1 case has shown that the ratings aren't consistent across all three sources: ERCOT Zonal Operations, Continuous = 717 MVA, 2 Hour = 717 MVA ERCOT Nodal DSV 21, Continuous = 717 MVA, 2 Hour = 717 MVA ERCOT SSWG 2010 Sum 1, Continuous = 956 MVA, 2 Hour = 956 MVA |  | Fixed with DSV 23 |  | [LUME 8/18/10] This line belongs to Oncor. LUME sent an email to Larry Reiter at Oncor to request that they figure out which ratings are correct and then submit model changes to correct the appropriate files.
30 | Congestion on Applied Energy (APD_ST1) | S_2073 APD_ST1 APD 138 APD 4.2 (08/05/10) | 2010-08-05 | ERCOT | Modeling/LDF Error | DAM/RUC | Severe congestion that is negatively impacting Houston Load Zone (HLZ) to Houston Hub spreads. DAM OD: 8/4/2010: Investigate non-adapting loads APD_APD_ST1 and APD_APD_AT1 which triggered very high shadow prices up to 50,000 $/MWH in DAM OD 8/4 A battery at station APD (Applied?) was introduced in DSV21 wih a LDF=80 MW that caused overloads with high shadow price and resulted in LZ_HOUSTON price to go upto $500. | sai | Closed- Fixed DSV23 |  | [ERCOT 8/5/2010] In DSV 21 additional changes were introduced in the network mdoel for APD. Further analysis and discussions with RE (submitting RARF for APD) has show that normal status of breakers were incorrect, LDF of one load APD_ST1 should be zero. This is in addition to rating change of line from deepwater to Applied that should be already in effect. With the normal status change (to OPEN) the contingency that is defined in DSV21 should be removed. [LUME 8/12/10] this constraint has occurred on 2 separate occasions between 8/4/10 and 8/5/10 and is typically associated with extremely high shadow prices (e.g. >$200,000). When this constraint is active, Houston Load Zone blows out over Houston Hub. A comment was made by ERCOT staff on the 8/5/10 conf. call that this is a step up xfmr that should be 'unchecked' for monitoring. Has this database change been made? [ERCOT 8/11/2010] ERCOT has changed this to a Non Conform Load and updated the load schedule. This change was submitted as part of the latest RARF update to the station which will be energized on 8/16 and will be in DSV23 (Scheduled NPROD date of 9/1/2010).
31 | DAM OD 8/4/2010: Generic constraint for import into DFW is incorrect in DSV 21 |  | 2010-08-05 | ERCOT | Modeling/Software bug | DAM/RUC/EMS | The incorrect definition of generic constraint for import into the DFW area uncovered a bug in the way generic constraints limits are checked in MMS. Fix is expected to come in with MMS 5 P9 patch - ETA into NPROD - beginning of septmeber. This caused delay in DAM execution for OD 8/4/2010 | sai | Closed- Fixed DSV23 |  | Fix required for modeling error of generic constraint. [ERCOT 8/11/2010] Correction is expected to become effective in DSV23 (Scheduled NPROD date of 9/1/2010).

## SAMPLE-DAM Report
DELIVERYDATE | HOURENDING | STL_PNT | TOTAL_DAM_ENERGY_BOUGHT | TOTAL_DAM_ENERGY_SOLD | TOTAL_PTP_OBL_AWARDED_SOURCE | TOTAL_PTP_OBL_AWARDED_SINK | TOTAL_CRR_NONDAMAWARDED_SOURCE | TOTAL_CRR_NONDAMAWARDED_SINK
2010-08-13 | 1 | HB_HOUSTON | 120 |  | 73.9 | 346 |  | 92.5
2010-08-13 | 1 | HB_HUBAVG | 1 |  | 122.9 | 270.3
2010-08-13 | 1 | HB_NORTH | 1546.4 |  | 37.3 | 357.2 |  | 226.4
2010-08-13 | 1 | HB_SOUTH | 326 | 2 |  | 306.7 |  | 232.7
2010-08-13 | 1 | HB_WEST | 365.2 | 20 | 63.3 | 97.8
2010-08-13 | 1 | LZ_HOUSTON | 1321 | 10.3 | 61.1 | 1074.8
2010-08-13 | 1 | LZ_NORTH | 2993 | 28.5 | 32.3 | 2169.9
2010-08-13 | 1 | LZ_SOUTH | 1166 |  |  | 1689.9
2010-08-13 | 1 | LZ_WEST | 935.1 | 2 | 31.1 | 107.6