## NATF Issues List
Source: NATF Issues List |  |  | http://www.ercot.com/calendar/2010/08/20100831-NATF
REF # | COMPANY | ISSUE CATEGORY | DESCRIPTION | PRIORITY provided by MP | ERCOT Lead | Status | ERCOT Comments | ERCOT Ranking
1 | PSEG | Competitive Constraints | Detailed discussion from ERCOT on how they plan to manage the generic constraints-- (W-->N and Hou import) | 1 | John Adams | Open | 8-30-10: ERCOT will calculate Generic Constraints two (2) days ahead of the operating period using power flow study cases for voltage stability constraints, and looking up limits from previously performed small signal stability constraints for known small signal stability issues (currently West-North). ERCOT plans to create these study power flow cases using COP data for the study period. Our intention is to use WRUC results to create these power flow cases, but this capability is not yet functional. Currently we are capturing a real-time case to exercise the generic constraint procedure. For voltage stability constraints, we calculate maximum transfer across the interface using the VSAT application, and then pass these limits to TCM (Transmission Constraint Manager) through manual entry with effective dates and times. For small signal stability (W-N) ERCOT examines the cases built for voltage stability constraints, and uses the generation units and lines in service data to look up in a table the small signal stability limit for that scenario based upon historic studies. TCM transfers these limits to market systems, where the execution of DAM captures these limits and incorporates them in the DAM run. The manual portions of this process are documented in ERCOT’s “Generic Constraint Limit Calculation Practice”. | 2
2 | PSEG | Competitive Constraints | Comparison of load flow cases with and without competitive constraints--we have no information on how this works yet. None of the competitive constraints were binding in the most recent test (24 hrs). So we still have no clue as to how the Step 1 and Step 2 SCED results differ. | 1 | Resmi Surendran/ Isabel Flores/Steve Reedy | closed | 8-30-10: Comparison of load flow cases is not in scope. ERCOT plans to use the "existing CSCs/CREs (See section 3.19) "Unless the Board approves changes, the Competitive Constraints" are the "existing CSCs/CREs ……. " Note that the W_TO_N generic constraint was active as competitve constraint during the recent 24 hr LFC test, from 11 P.M. on 19th to 6:45 A.M. on the 20th and then from 10:45 A.M. to 12:30 P.M. on 20th. Note that from 12:35 AM to 1:30 A.M. the price separation was due to W_TO_N since that was the only constraint that was binding during that time. Also, during the recent 40 hr LFC test the N-H generic constraint was active. | 3
3 | CPS | DAM & RT Credit | If a QSE has a negative credit limit and submits a TPO, then the system will not allow for the cancellation of the TPO if this action would result in the credit line remaining negative. | 1 | Sai Moorty | open | 8-30-10: Implemented as per NPRR 206. Can discuss further - Not a defect. 9-3-10: This was discusssed at the 8-31-10 NATF. Sai to research. | 3
4 | LCRA | Settlement Price Calculations | Irrational settlement point prices are a concern seen in Market Trials and not acceptable for go-live. Settlement point prices were reported as zero or negative market wide. There have also been large price swings from a high positive number to a large negative number and back to a high positive number in the span of five 15-minute intervals. These results do not seem to be logical or reasonable. | 1 |  | closed | 8-30-10: ERCOT has not observed irrational Settlement Point Prices. Specific issues observed in the past have been addressed and have been explained. Output data from SCED has been consistant with the input data. If you need explanations for specific intervals, please send in specifics to MarketTrials@ERCOT.com. | 5
5 | CALPINE | LFC | During LFC's we would like to see ERCOT using a CPS1 minimum of 125% rather than 100% | 1 |  | closed | 8-30-10: NERC criteria is 100%, ERCOT will continue to report the CPS1 scores from the LFC tests. | 5
6 | Luminant | DAM Clearing Engine | If number of source/sink pairs for CRR PTP Options carried to Real-Time exceed 100, increases iteration time for DAM. Prohibits correct modeling of Phase Shifters as in the field. | 1 | Sai Moorty | open | 8-30-10: DAM optimization cannot solve for both Phase Shifters optimization and PtP Options (complex solution that was not considered years ago during design when there were no PSTs). As discussed in DeepDive mtgs, ERCOT working on procedure to improve PST with 1) Moving off of neutral position based on weather forecast from Operations. 2) "Monitor Only" those lines affected by the PSTs. Note there is only 1 setting for each PST for the 24-hour period. | 2
7 | Luminant | Network Modeling | The network model used for DAM should be consistent with the real time model with regard to all mitigation plans, SPSs, etc. and there should be a verifications process to check for consistency prior to go-live. | 1 | John Adams | open | 8-30-10: John Adams is finalizing procedures. Draft Procedures to be provided by 9-8-10. | 1
8 | NRG | Real-Time Operations | Discussion from ERCOT on the XML messages utilized when deploying non-spin. Are the XML messages the same for off-line generation resources, on-line generation resources, controllable load resources and non-controllable load resources? Will market participants get an opportunity to test the non-spin deployment messages? | 1 | Resmi Surendran | closed | 8-30-10: This item came in separate from the original list. As part of Market Trials, we had done some open loop testing of the NSRS deployment. Also, during the 40 hour LFC test, NSRS was deployed. If still needed by NRG or others, additional tests can be scheduled. | 5
9 | Luminant | DAM Clearing Engine | ERCOT needs a proven methodology for load distribution factors and allocation of non conforming loads. | 2 | Sai Moorty/ John Adams/ Matt Mereness | open | 8-30-10: Currently using data from 7 days ago as discussed in protocols and seeded with State Estimator data. ERCOT is working on establishing an alternative procedure for establishing LDF. In DAM, every submission at the Load Zone is distributed down to individual loads as conforming load as per the protocols. | 2
10 | Luminant | DAM Clearing Engine | Due to rounding AS quantities awarded to the nearest tenth, the awarded quantities actually exceeded offers by 0.10 to 0.20 MW | 2 | Sai Moorty | Open | 8-30-10: Investigating the following change (details to be provided in September NATF): 1) Adjust the individual block awards sent to market participants from MMS to match total that S&B recieves. 2) Need to check if this type of adjustment does not break something else - AS OFFER CAP management. Working to correct this, but ERCOT does not consider this item as absolutely necessary for go-live. | 3
11 | Luminant | DAM Clearing Engine | Is there a need for a protocol revision to create shadow price limits in DAM equal to Real Time? | 2 | Sai Moorty | deferred | 8-30-10: Not necessary for go-live. | 5
12 | Luminant | Network Modeling | Network model used for DAM must include PCAPS used in Real Time model. | 2 | John Adams | closed | 8-30-10: ERCOT agrees. See the answer for REF # 7. | 2
13 | Luminant | Network Modeling | ERCOT has provided redacted operations model files and evaluation is ongoing concerning review of operations model files. | 2 | Sai Moorty | closed | 8-30-10: Per NPRR202 redacted model is posted for each model load, and PSSe file being provided for market trials. | 5
14 | Luminant | Network Modeling | Is there a different methodology or set of ratings being used between the nodal (reported as RTM) and zonal (reported as Daily Ops) models. Is ERCOT working with the TDSPs to match/correct these differences? | 2 | Matt Mereness/ Anthony Natoli | closed | 8-30-10: Each TSP is required to submit to ERCOT its rating methodology. There is no provision for different methodologies between Zonal and Nodal. Nodal to Zonal comparisons have been made. Any reports of discrepancies are passed on to TSPs by ERCOT. | 5
15 | Luminant | Network Modeling | Luminant tracking approximately 12 active Modeling issues on DAM Deep Dive calls. ERCOT Ownership of the quality of the data based on the Current Network Model for DAM and RT. | 2 | Matt Mereness/ Woody Rickerson | open | 8-30-10: Covered on DAM Deep Dive list. ERCOT has developed a model quality assurance process prior to model first use. This process is part of the 90 day model review process described in the protocols. | 2
16 | Luminant | Line Ratings | Luminant tracking approximately 19 active ratings issues on DAM Deep Dive calls. ERCOT Ownership of the quality of the data based on the Current Network Model for DAM and RT. | 2 | Matt Mereness/ Woody Rickerson/Anthony Natoli | open | 8-30-10: Covered on DAM Deep Dive list. ERCOT has developed a model quality assurance process prior to model first use. This process is part of the 90 day model review process described in the protocols. | 2
17 | Luminant | Real Time Operations | All questions, comments, and observations dealing with start up and shut down of units. | 2 | Dave Maggio | open | 8-30-10: ERCOT Business Practices for "ERCOT and QSE Operations During the Operating Hour" should address these issues. First Draft scheduled to be reviewed at 8-31-10 NATF. | 5
18 | Luminant | Real Time Operations | Questions and comments regarding the real time telemetry of AS responsibility on units varying during the Operating Hour. | 2 | Dave Maggio | open | 8-30-10: ERCOT Business Practices for "ERCOT and QSE Operations During the Operating Hour" should address these issues. First Draft scheduled to be reviewed at 8-31-10 NATF. | 5
19 | Luminant | Real Time Operations | QSE AS Capacity Compliance Monitoring Notification: ERCOT will supply a notification to QSEs when the comparison between the QSEs AS Supply Responsibility in the EMS system with the AS Supply Responsibility in the MMS system indicates that the QSE is not providing sufficient capacity Question: will the notification also be available through XML form, similar to EIP 1.19, section 5.3.1.2? Outstanding question. | 2 | Colleen Frosch | deferred | 8-30-10: ERCOT notifies Participants in advance of capacity shortages based on COP info with XML messages. ERCOT performs RT notification with phone calls until XML notification is added post go-live. ERCOT also provides a 5 minute report. | 3
20 | Luminant | Market Data/Reports | Question: When will QSE Ancillary Services Capacity Monitor report on the MIS or through Get Reports be available? Response: report is not active at this time, release data is not yet established. The Report will only work when Telemetry is required for DAM awards | 2 | Jamie Lavas | open | 8-30-10: Though required by Market Trials, we have had several outstanding defects with this report. It is currently back in development and will be re-released to itest next week for further testing. Once through itest, it will need to be validated by business before it can be released in nprod. if business or itest find additional defects, it will be remanded back to development again. Still working to get an estimate for the delivery date. | 2
21 | Luminant | Protocol Revision | When DAM is aborted, ERCOT will not have AS to meet their obligations. ERCOT will abort the DRUC and run a SASM, in which offers can be revised. Need approval of NPRR255. | 2 | Matt Mereness | open | 8-30-10: Yes. On 8/19/10, PRS unanimously voted to recommend approval of NPRR255 as submitted. | 5
22 | Luminant | Settlement | The ERCOT settlement system is incorrectly using HSL from the COP to detect curtailed intervals. Needs a system change or work around. Settlement of BPD not right for non-IRR units. Calculation is wrong. | 2 | Mandy Bauld | open | 8-30-10: BPD for IRR: ERCOT system is coded per protocol. The issue (can the market go-live per that protocol) is open at QMWG/WMS. ERCOT's slides for QMWG update at the 8/18 WMS offered options for an interim solution; options would require a protocol change, but not a system change. ERCOT is still investigating whether or not there are other viable options. BPD for non-IRR: ERCOT system AABP calcluation is coded per protocol. Luminant submitted a question to market trials concernign the validity of the protocol calculation, under a scenario when any of the SCED intervals in the 15-minute settlement interval are less than 5 minutes. ERCOT staff is currently addressing this question. Luminant has been asked to provide data to backup their concern. ERCOT does not believe there is an issue with BPD for non-IRR. More discussion is needed. Absent a timely NPRR the current Protocols will be in effect. | 5
23 | Luminant | Compliance Criteria | Anticipating some questions will be answered in ERCOT Real Time Business Practices document. | 2 | Kenneth Ragsdale | open | 8-30-10: Document to be posted and reviewed at 8-31-10 NATF meeting. | 5
24 | Luminant | Real Time Operations | Need submittal and approval of NPRR to add protocol language for real time dispatch of units in SCED | 2 | Kenneth Ragsdale | open | 8-30-10: Need better description of the issue. | 5
25 | Luminant | Resource Parameters | Would like ERCOT to: 1) Provide QSEs ability to view the values ERCOT is using in their modeling. 2) Provide a method of correcting this number should the ERCOT value get out of sync with the units actual status | 2 | Kenneth Ragsdale | open | 8-30-10: Need better description of the issue. QSEs have the ability to update operational resource parameters and can view most of the values. | 5
26 | Luminant | Planned Telemetry Outages | ERCOT compliance criteria for telemetry does not take into account planned outages. | 2 | John Dumas/ Alex Sills | open | 8-30-10: NOGR 34 is scheduled to be reviewed at the September BOD meeting. | 5
27 | Luminant | Compliance Criteria | The language in the NPRR for telemetry of WGR HSL is overly restrictive; may need modifications. | 2 | Dave Maggio | closed | 8-30-10: See answer to REF # 30 below. | 5
28 | LCRA | Market Data/Reports | Future Credit Exposure for CRR PTP Options (FCEOPT) Detail Report | 2 | Cheryl Yager | open | 8-30-10: This detailed report is not currently being provided and is not expected to be provided as it takes too long to run. NPRR 241 (going to TAC next week) allows ERCOT to not provide this report and/or allows ERCOT to provide an extract instead. ERCOT is working on an extract of the data. | 3
29 | LCRA | Market Data/Reports | Future Credit Exposure for CRR PTP Obligations (FCEOBL) Detail Report | 2 | Cheryl Yager | open | 8-30-10: This detailed report is not currently being provided and is not expected to be provided as it takes too long to run. NPRR 241 (going to TAC next week) allows ERCOT to not provide this report and/or allows ERCOT to provide an extract instead. ERCOT is working on an extract of the data. | 3
30 | E.ON Climate & Renewables | Protocol Revision | Issue of ERCOT producing a curtailment flag for Wind Resources to the list with a priority of #2? There was an NPRR that stated that if your basepoint is 2 MW less than your HSL sent into ERCOT, the resource is curtailed, but it has become evident during the LFC testing that a curtailment flag is truly the only reliable way a wind resource can be assured of a curtailment. We have a few QSEs for our many wind farms and each QSE has their own calculation for when a wind resource is curtailed and each method is different. If wind QSE's formula for calculating a curtailment is wrong, there could be reliability issues on the system. | 2 | Dave Maggio | closed | 8-30-10: The language in the protocols (as a result of approved NPRR 214) is clear. ERCOT is not planning to submit NPRRs to change the approach. | 5
31 | CALPINE | RUC | Calpine would like the ability to move AS onto a unit that has been committed for RUC. Currently ERCOT allows this by calling ERCOT and the operator can turn down the request. If a unit trips, then ERCOT has no choice but to accept the request. Calpine would like a rules based response to any request to move AS and would prefer that the request be handled systematically via an electronic transaction as opposed to simply operator judgement. | 2 | Colleen Frosch | closed | 8-30-10: Per Section 3.9(4), moving AS to a Resource RUCed on is not permitted . Not required for go-live. | 5
32 | CALPINE | DAM | Request for all Combined Cycle resources to be allowed to change their offer curve in the adjustment period. We realize this is an item that was discussed at length in past years, however, we believe the market has learned a lot about CC resources since then and it would be productive to re-open this issue. As a middle ground the request could be softened to allow any Co-gen (QF) to change their offer curve in the adjustment period and disallow any other type of resource to make changes. Two other alternatives for consideration are changes during the Adjustment Period and Inter-Hour again for Co-gen purposes. | 2 | Steve Reedy | closed | 8-30-10: Implemented according to protocol. | 5
33 | CALPINE | Competitive Constraints | We want to be able to verify the classification of non-competitive constraints. Right now we see the results but not the process. The list of competitive constraints seems too small. | 2 | Resmi Surendran | closed | 8-30-10: See answer to item 2 above. | 5
34 | CALPINE | Protocol Revision | NPRR200 was approved in Feb 2010 and essentially says that DC-Tie schedule data will be sourced from the OATI system. ERCOT has been very slow to respond with details regarding how QSE's will access DC-Tie data. As of August 2010, ERCOT is now pulling DC-Tie schedules from the OATI zonal system and settling them in Nodal settlements. However, ERCOT has indicated no plans to provide any type of download for QSE systems to determine trade positions or for shadow settlements purposes. | 2 | Scott Middleton/ Mandy Bauld | closed | 8-30-10: QSE's should access DC-Tie data through OATI. Settlement extracts (RTM CODE) contain the DC Tie data used in settlment, which is sourced from the OATI system. The published DC Tie-related billing determinants include: RTDCEXP, RTDCIMP, DCIMPSNAP, and DCIMPADJ. The LSEGUFE for approved import tags will be included in the RTAML at the DCTIE Settlement Point and will also be in the RTM CODE extract. | 2
35 | CALPINE | AS on a RUCed Resource | If the ERCOT Operator RUCs a Combined Cycle Resource to a different configuration and the Resource was already carrying AS on the train ----- can they continue to carry AS on the train? Can a resource holding AS be committed for RUC? Can a resource be RUCed that is already holding AS? Section 5.5.2(7) seems to indicate that a resource already holding AS cannot be committed for RUC. However, we’re not sure to what extent ERCOT could use the “infeasibility” exception in this paragraph. Furthermore, if the configuration committed for RUC was not carrying AS, would we be allowed to move the AS to that config (see separate question next that references section 3.9(4)). What if the config confirmed for RUC could not provide the AS, would ERCOT relieve us of the obligation to provide AS? | 2 | Colleen Frosch | closed | 8-30-10: This item came in separate from the original list. A Resource will be RUCed to a different configuration only by an ERCOT Operator (ie not by the software). If the grid needs additional capacity, then ERCOT could direct a different configuration which would provide this additional capacity. If ERCOT asks for a configuration which would yield an increase in capacity without directing that this capacity be used to provide AS, then the AS should be moved to a different Resource. Section 5.5.2(7) indicates that a RUCed Resource cannot carry AS unless it was RUCed on to provide AS. | 5
36 | Luminant | Market Data/Reports | Forecasted Temp. Adj. Dynamic Ratings Duplicate Data: Each timestamp row of data is duplicated | 3 | Jamie Lavas | open | 8-30-10: This is an open defect. Expected to be fixed in NPROD by dd/mm/yy. | 3
37 | Luminant | Market Data/Reports | Shift Factors Rpt Duplicate Records: Each timestamp row of shift factor data is duplicated | 3 | Jamie Lavas | open | 8-30-10: This is an open defect. Expected to be fixed in NPROD by dd/mm/yy. | 3
38 | Luminant | Compliance Criteria | Whether the PUC intends to change its QWETR rule in any way to reflect the nodal market. New PUC project was opened. | 3 | Kenneth Ragsdale | closed | 8-30-10: This is not within ERCOT's scope. (Quarterly Wholesale Electricity Transaction Reports.) | 5
39 | Luminant | Systems I/O | It seems that messages of type = TELEMETRY do not have milliseconds and type = Market Message do have milliseconds. Is this the intended behavior for alerts? Can we expect this to be how this field is populated? | 3 | Jeff Gilbertson | closed | 8-30-10: While the format of the timestamps are inconsistent, they are valid formats. Yes, the timestamps will continue to be populated in this manner. | 5
40 | Luminant | Real Time Operations | Advocate to change SCED to use an integrated value on the ramp rate curve. The way SCED behaves now, if the unit is currently at 5 MW/min rr and on the cusp of the next ramp rate at 10 MW/min rr, SCED will continue to use 5 MW/min rr even though the unit is capable of providing more than 5 MW/min. | 3 | Kenneth Ragsdale | closed | 8-30-10: Could be considered post go-live. This would be a change in scope. | 5
41 | Luminant | RUC | HRUC notices are received after the COP deadline has passed. Possibly solved. | 3 | Scott Middleton | open | 8-30-10: There was a one time occurance of this from the HRUC software during Market Trials, the root cause was a late web report, and the issue was resolved. It is possible for this to occur in the case of RUC VDIs; this issue will be added to the COP Expectations Business Practices. | 3
42 | Luminant | Systems I/O | Do “Emergency Notice” alerts only show up on the MMS? | 3 | Jamie Lavas | closed | 8-30-10: Assume the question was MIS not MMS?. Public alerts are posted to the MMS UI, MIS and the EIP listener.
43 |  | Additional resource status for resource startup/shutdown | ERCOT published guidelines for telemetry and resource statuses during resource startup and shutdown. We would like additional resource statuses for conditions below LSL rather than using workarounds with existing resource statuses. | 2 |  |  | 8-31-10: This was added at the 8-31-10 NATF meeting.
44 |  | Trade Confirmation Timestamp | ERCOT has not implemented a trade confirmation timestamp in the Trades area on the MMS. Although notifications provides a timestamp of when each QSE submits or confirms this can provide conflicting timestamps particularly when confirmation is done around 1430. A single timestamp record is needed on the Trades tab to confirm which RUC capacity will be treated in. This leaves a hole for shadow settlements to determine whether a trade was confirmed pre or post 1430. | 2 |  |  | 8-31-10: This was added at the 8-31-10 NATF meeting.
45 |  | DA/RT SPP Price files only available for 3 days on MIS | The RT SPP Price files are only available for 3 days on MIS and DA SPP Price Files for 5 days. We have asked ERCOT to increase this to at least 7 days to ensure if there are download errors sufficient time is allowed to correct the issue. Other ISO's observe posting times of 7 days and greater for prices. This becomes the greatest issue over weekends when reduced vendor and technical staff cannot realistically solve a technical issue in time before data rolls off the MIS. | 2 | Kenneth Ragsdale | closed | 8-31-10: This was added at the 8-31-10 NATF meeting. 9-3-10: ERCOT has increased the holding time for 5 & 15 min LMP/SPP files to 5 days.
46 |  | PRDE Files only on MIS for 2 days | Currently the PRDE files are only out on the portal for 2 days. We have asked ERCOT to increase this to at least 7 days to ensure if there are download errors sufficient time is allowed to correct the issue. This becomes the greatest issue over weekends when reduced vendor and technical staff cannot realistically solve a technical issue in time before data rolls off the MIS. | 2 | Kenneth Ragsdale | closed | 8-31-10: This was added at the 8-31-10 NATF meeting. 9-3-10: The historical PRDE files are not necessary for loading historical extracts.
49 |  | Approval of the procedure describing how to set shadow price caps and power balance penalities in SCED | Per Nodal Protocols 6.5.7.1.11, ERCOT shall determine the methodology for setting maximum Shadow Prices for network constraints and for the power balance constraint. Following review and recommendation by TAC, the ERCOT Board shall review the recommendation and approve a final methodology. Many market participants believe this procedure needs to finalized before one can vote on a go-live decision. | TBD |  |  | 8-31-10: This was added at the 8-31-10 NATF meeting.
50 |  | Approval of the procedure which sets the x,y, and z variables for the GREDP compliance claculation. | Per Nodal Protocols 8.1.1.4.1,the GREDP/CLREDP performance criteria in paragraphs (7) through (9) shall be reviewed and set by the TAC two months before the Texas Nodal Market Implementation Date (TNMID). The performance criteria will be subject to review by TAC beginning two months after the TNMID and as deemed necessary. The GREDP/CLREDP performance criteria variables X, Y, and Z shall be posted to the MIS Public Area no later than three Business Days after TAC approval. | TBD |  |  | 8-31-10: This was added at the 8-31-10 NATF meeting.
51 | LCRA | TBD | In order to test our software implementation which calculates the Startup Offer Cap and Minimum Energy Offer Cap, ERCOT needs to start incorporating the FIP adder and Proxy Heat Rate when validating Offers. | 1 |  |  | 9-3-10: This was added 9-3-10.

## Legend
LEGEND
1 = Show stopper; Needs resolution before Go-live can be accomplished.
2 = High priority issue that should be resolved by Go-live. Work-Arounds could be developed but for a very short time frame.
3 = Needed but can be implemented post Go-live. Will not affect safety, operational reliability or validated work-arounds exist.
4 = Needed by Planning Go-Live (approximately March 2011)
5 = Not an issue. (Could be an answer to a question or a discussion item.)