ERCOT Process for Evaluating Asynchronous Ties

Applicability

This basic process shall apply to all asynchronous ties between ERCOT and other transmission networks that are proposed on or after January 1, 2010.  For the purposes of this process document, a commercial asynchronous tie is defined as a tie that is primarily intended to allow commercial transactions to, from or over the ERCOT system, or that in ERCOT’s reasonable opinion could have a material impact on energy prices or costs in the ERCOT markets. This process will not apply to emergency load transfers between ERCOT and other networks that are not simultaneously connected to both networks, such as block load transfers.  The process may be modified as deemed necessary by ERCOT to meet the unique circumstances associated with each specific proposed tie, while maintaining the non-discriminatory nature of the process.

Limitations

This process is intended to cover the transmission system engineering studies that would be necessary for evaluating an asynchronous tie between ERCOT and another transmission network.  It does not address the process for obtaining regulatory approval (from FERC, PUCT, etc.) that may be necessary for such projects.

Notification

The entity, “Proposer,” that would construct and/ or own the asynchronous tie interconnection facilities (that is, facilities to interconnect the ERCOT grid to a system outside the ERCOT grid) shall submit notification to ERCOT (via the rpg@ercot.com mailbox) describing the proposed facilities.  Within five (5) business days of receiving the notification ERCOT will designate a TSP to lead the reliability study and contact that TSP to schedule a reliability study scope meeting.  ERCOT will select the lead TSP based upon its preliminary analysis with respect to the most likely point of interconnection.  The lead TSP may be the same as the Proposer.

At the same time ERCOT will send notification of the project to all other TSP(s) via the confidential Transmission Owner Generation Interconnection email list.  It is the responsibility of each TSP to determine if the proposed project would have a material impact on their transmission facilities and to what extent they should participate in the reliability study.  Each TSP desiring to participate in the reliability study should notify the lead TSP.  The lead TSP will have the responsibility to involve all other TSP(s) that have expressed an interest in the reliability study as appropriate for their expressed level of involvement to the extent that such involvement is reasonable.

Reliability Study

A reliability study will be performed for all asynchronous ties.  The reliability study shall consist of the following elements:

- Steady state analysis

- Short circuit analysis

- Stability analysis including:

  - Transient stability analysis

  - Voltage stability analysis

  - Frequency stability analysis (testing of loss of the tie, consistent with Table 1 of the NERC TPL standards, during both maximum import and maximum export conditions)

  - Subsynchronous resonance/ Subsynchronous interaction analysis testing the impact on nearby generation that may be affected

Following the completion of the reliability study, the lead TSP will present the results to ERCOT and other TSPs via the confidential Transmission Owner Generation Interconnection email list.  ERCOT and TSPs will have ten (10) days to provide comments.  Any transmission projects deemed necessary by the reliability studies shall undergo the Regional Planning Group (RPG) review process according to the appropriate Tier classification of the project.

Economic Study

Any commercial asynchronous tie shall also undergo an economic evaluation.  The scope of this economic study will include the determination of the set of incremental transmission system improvements that would be economic should the asynchronous tie be constructed.  The scope of the economic study may include an assessment of the overall economic impact of the asynchronous tie to the ERCOT market; however, this assessment will not be considered by ERCOT unless needed to evaluate the economics of any incremental transmission system improvements that are warranted by the addition of the tie and that would be included in transmission cost of service paid for by ERCOT loads, or unless ERCOT is so directed by the PUCT.

The Proposer shall submit a description of the project and an economic study scope to ERCOT.  ERCOT will forward the description and study scope to the RPG, which will have 21 days to provide comments.  The Proposer will have up to 28 days to resolve the comments from the RPG.  If all of the comments cannot be resolved, ERCOT will determine the approach that should be included in the economic study to address the comment.

At the end of the RPG review period the Proposer will fund the analysis, to be performed by an independent consultant, described in the economic study scope.  The entity that performs the economic study shall allow ERCOT, in conjunction with the affected TSPs, to propose transmission upgrade projects to relieve congestion on the ERCOT system.  The following study results will then be presented to ERCOT for each set of proposed transmission upgrade projects:

- Projected production cost changes on the ERCOT system

- Projected energy revenue (generator revenue) changes on the ERCOT system

- Export MWs times the asynchronous tie LMP (ERCOT side) summed for all export hours

- Import MWs times the asynchronous tie LMP (ERCOT side) summed for all import hours

- Sum of export tariff charges and an explanation of how this was calculated

- List of congested elements and magnitude of the congestion on each element before and after the addition of the tie and any related system upgrades

- List of asynchronous tie flows for the duration of the analysis

Once ERCOT is satisfied that the set of transmission system improvements that may be economic should the asynchronous tie be constructed has been found the Proposer and/or affected TSPs shall present their findings to the RPG and will provide an opportunity for the RPG to comment and for the Proposer to respond to those comments.

ERCOT Review

ERCOT will not recommend or endorse commercial asynchronous ties or associated AC transmission system improvements.  However, ERCOT will provide an independent report that:

- assesses how well the study addressed the comments of ERCOT and the RPG;

- provides independent comments on the study; and,

- provides a contingent assessment of the incremental transmission projects on the ERCOT system that are indicated by the study.

Notice to Proceed

The interconnecting TSP shall inform ERCOT once it has signed an interconnection agreement with notice to proceed for the asynchronous tie facilities and the Proposer will inform ERCOT when it has signed an interconnection agreement with a notice to proceed with entities on the other transmission network.  At this point the project will be added to the base case models.