ERCOT OPERATIONS REPORT

ON THE EEA EVENT

OF

August 20, 2010

Executive Summary	3

Time Line and Description of Significant Events	4

Observations/Data Review	6

ARR, RRS and NSRS	6

Adjusted Responsive Reserve Available, Responsive Reserve Deployed, NSRS and ERCOT Taylor Frequency.	7

High-Speed Frequency Recorder Data	8

ACE and ERCOT Taylor Frequency	9

LaaR response and ERCOT Frequency	10

Action Items and Lessons Learned	11

Executive Summary

At approximately 15:25:48 on August 20th, 2010, unit A at the 345 kV Station A tripped causing the loss of approximately 1319 MW of generation in the Houston area due to an inadvertent turbine trip signal initiated during planned surveillance testing.

Approximately eight seconds later, unit B at the 138 kV Station B tripped offline. At approximately 15:31:56 unit C tripped, and at approximately 15:32:36 unit D tripped.  The total loss of generation from this west Texas plant was approximately 212 MW.

ERCOT ISO Operations responded to this event as a NERC Disturbance Control Standard event; however it should be excluded from compliance evaluation for being larger than the single largest contingency event. ERCOT ISO historical (PI) data indicates that frequency dropped to approximately 59.749 Hz immediately after the first trip of unit A. The system frequency recovered to 60 Hz in approximately 4 minutes and 42 seconds (~15:30:30). ERCOT ISO recovered from the frequency deviation as required by the NERC Reliability Standard BAL-002-0.

At 15:25:48, 1150 MW of Generation Responsive Reserve was deployed due to the low frequency. These reserves were deployed at the beginning of the event, along with approximately 20 MW of Load acting as Resources (LaaRs), which tripped on under-frequency relay action. At 15:28 ERCOT ISO requested all Qualified Schedule Entities (QSE) to deploy all remaining LaaRs scheduled to provide Responsive Reserve Service.  A total of 1320 MW of LaaRs were deployed.

At 15:41, all QSEs were instructed to restore LaaRs.  Non-Spinning Reserve Service (NSRS) was deployed at 15:44 in the Houston zone for interval ending 16:15, and 15:45 in the South, North and West zones for interval ending 16:30.  ERCOT ISO implemented Level 1 of its Energy Emergency Alert (EEA) at 15:48 due to Adjusted Responsive Reserve (ARR) dropping below 2300 MW.  By 16:13:38, ARR was above 2300 MW and EEA Level 1 was cancelled at 16:35.

The following operations report discusses primary and contributing factors leading up to and during the EEA event and action items that ERCOT has taken in response to the event.

Time Line and Description of Significant Events

8/20

- 15:25:40 ERCOT system frequency prior to disturbance was 60.0149 Hz.

- 15:25:48 Unit A at Station A was operating at 1319 MW, tripped to zero.

- 15:25:48 ERCOT system frequency dropped to approximately 59.749 Hz immediately after the trip.

- 15:25:48 1150 MW of Generation Responsive Reserve was deployed automatically in response to the frequency spike.

- 15:25:56 Unit B at Station B was operating at 75 MW, tripped to zero.

- 15:28 Hot-line called made to all QSEs to deploy all LaaRs and Hydro supplying Responsive Reserve.

- 15:30:30 ERCOT system Frequency recovered to 60 Hz.

- 15:31:56 Unit C at Station B was operating at 66 MW, tripped to zero.

- 15:32:36 Unit D at Station B was operating at 71 MW, tripped to zero.

- 15:33 Watch issued for ARR below 2500 MW.

- 15:35:34 ARR dropped below 2300 MW.

- 15:38 ERCOT ISO made request for emergency energy across the CFE DC-Ties.

- 15:41 Hot-line call made to all QSEs to restore LaaRs and Hydro supplying Responsive Reserve.

- 15:44 ERCOT ISO directed one QSE to lower fleet generation by 400 MW due to high frequency caused by LaaR deployment.

- 15:44 NSRS was deployed in the Houston zone for IE 16:15.

- 15:45 NSRS was deployed in the South, North and West zones for IE 16:30.

- 15:48 Hot-line call made to all QSEs to notify them that ERCOT declared EEA Level 1 for adjusted Responsive Reserve below 2300 MW.

- 15:53 ERCOT ISO contacted the Southwest Power Pool (SPP) to inquire about available transmission service across the SPP DC-Ties.  ERCOT ISO was informed that there was 76 MW of transmission service available across the North Tie.

- 15:59 ERCOT ISO contacted one QSE to inquire about available capacity up to the 76 MW.

- 16:00:06 183 MW of NSRS came on-line in the Houston zone.

- 16:15:06 Additional 777 MW of NSRS came on-line in the remaining zones, for a total of 960 MW.

- 16:29 ERCOT ISO released one QSE of instruction to lower fleet generation by 400 MW.

- 16:35 EEA Level 1was cancelled.

- 18:19 Watch issued for Adjusted Responsive Reserve below 2500 MW was cancelled.

### Observations/Data Review

- 08/20/2010 15:00 – 19:00 ARR, RRS and NSRS

Figure 1 ARR Available, Responsive Reserve and Non-Spin Deployed.

- 08/20/10 15:00 – 19:00 Adjusted Responsive Reserve Available, Responsive Reserve Deployed, NSRS and ERCOT Taylor Frequency.

Figure 2 ARR Available, Responsive Reserve Deployed, NSRS Deployed and ERCOT Taylor Frequency.

- 08/20/10 15:25 – 15:26 High-Speed Frequency Recorder Data

Below is a graph of the ERCOT ISO High-Speed Frequency Recorder Data.  This data indicates that ERCOT system frequency dropped to approximately 59.748003 Hz at approximately 15:25:50.614.

Figure 3 ERCOT High-Speed Frequency Recorder Data on August 20, 2010.

- 08/20/10 15:00 – 19:00 ACE and ERCOT Taylor Frequency

Figure 4 ACE and ERCOT Taylor Frequency.

- 08/20/10 15:15 – 16:15 LaaR response and ERCOT Frequency

Figure 4 LaaR Response and ERCOT Frequency

### Action Items and Lessons Learned

Event report provided by Station A owner:

The owner reported to ERCOT System Operations that an automatic reactor trip occurred while the plant was stable at 100% power. The reactor trip was caused by an inadvertent turbine trip signal initiated during planned surveillance testing and unit A at Station A tripped losing approximately 1319 MW of generation. All systems actuated as designed. The Station A unit A main generator output breaker operated as designed. Corrective actions are being developed to prevent recurrence in accordance with the Station A corrective action program.

Event report provided by Station B owner:

Unit B, unit C and unit D at Station B were disconnected from the grid losing approximately 212 MW of generation due to a system frequency dip, resulting in the turbine from unit B to drop to to 3585 rpm.  The unit responded by opening high pressure control valves, and subsequently tripped the steam turbine on fourth stage pressure high. Unit C and unit D tripped on excess steam flow. The station owner is investigating alternatives to allow for frequency deviations as large as what occurred during this event.