## Slide 1: PDCWG Report to ROS
September 16, 2010
Sydney Niemeyer

## Slide 2
CPS1 = 160.97

## Slide 3
Nodal 24 hr test. Aug 4 noon to Aug 5 noon. CPS1 = 130.00 for test period.
Nodal 40 hr test. Aug 26 10 am to Aug 28 2 am. CPS1 = 141.96 for test period.
Nodal 24 hr test. Aug 19 noon to Aug 20 noon. CPS1 = 137.03 for test period.
Aug 19 – 20 LFC test CPS1 without HE0600 on the 20th would have been 146.40
HE06 CPS1 = -78.49 HSL Nodal problem
HE16 CPS1 = -256.35 DCS EEA event.
Contributing factors for low score:
Unit trip @ 14:32 with slow recovery.
Out of down reg:
IE1515 to IE1530
IE1615 to IE1700
QSE Balancing error IE2345

## Slide 5
of ERCOT Frequency

## Slide 6
Aug 1, 7 & 8 Sun, Sat & Sun
Aug 20 DCS & EEA event

## Slide 7
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 148.13

## Slide 8: Status as of August 5, 2010
Units with Governors presently set with an intentional deadband less than or equal to +/-0.01666 Hz and droop curve with no step function.
  14,258 MW Total Capacity Identified by PDCWG members.
    1690 MW Lignite
    5534 MW Coal
    3780 MW Combustion Turbine Combined Cycle
    1519 MW Combustion Turbine Simple Cycle
    1224 MW Steam Turbine – natural gas fired
    240 MW Hydro
    271 MW Wind Generators

## Slide 11
Same 600 MW unit MW movement due to frequency each year.

## Slide 12: Factors Other Than Governor Changes That May Have Contributed to Improved Frequency Performance
MCPE in 2008 was more volatile than 2010
More non-conforming load in 2008.
Natural gas price volatility in 2008.
NERC Reliability Standard enforcement since 2008.
Improved Operations at ERCOT, GO’s and GOP’s.
14 minute ramp implementation in October 2008.
LFC tuning in early 2008.
Hurricane Ike arrived in September 2008 with loss of significant load in Houston.

## Slide 13: Historical Frequency Response (Next three slides)
Data for events from 1994 to present for Point C and Point B evaluation. Point B+30 evaluation began in 2003.
Long term trend is increasing performance on each evaluation.
Short term trend (rolling average of last 40 events) since early 2009 indicates some slight decline in performance.
Evaluation does not include LaaR response on any of the events.

## Slide 17: ERCOT Total Load and Wind Generation
Data source not EPS quality.
Confidence in data good with some telemetry errors scrubbed.
Next three slides for reference only.

## Slide 21: DCS Event August 20, 2010
Interconnection Primary Frequency Response met minimum requirement at the B and B+30 evaluation points.
Six QSE’s did not deliver RRS within 10 minutes.
  Two of these QSE’s did not appear to attempt to deliver RRS. Further investigation needed to determine cause.
Four QSE’s with RRS obligations did not meet minimum Primary Frequency Response performance.

## Slide 22: Nodal LFC Testing
CPS1 scores improved during last two tests.
  LFC controlling to scheduled frequency instead of target CPS1 value.
  Regulation deployment tuned similar to Zonal LFC.
  Frequency control during Resource Start-up and Shutdown seems to be one area where improvement is needed. In Zonal, the QSE managed the Start-up and shutdown by following the 14 minute Base Power Schedule ramp and measured performance with SCPS2. In Nodal, SCED and LFC must manage these ramps in a reactionary response.
GREDP
  Need clarification of which LSL is used by GREDP.
    Market Trials reports that the telemetered value is used.
    TRE reports that the RARF value is used.
  If the telemetered LSL is used and the QSE updates the LSL to track actual output during startup and shut down, the Resource performance measurement continues impacting Resource score.
  SCED does not consider Up Reg Responsibility in calculating LDL. If Up Reg is recalled (consuming down ramp rate of the Resource) during Base Point change that consumes the full Down ramp rate of the Resource the Resource will not be able to keep up with both deployments. This occurs when the Resource has Up Reg Responsibility and zero or little Down Reg Responsibility. The reverse situation can also occur.
  SCED timing issue across the top of the hour with changes in Reg Responsibilities.

## Slide 23: Next PDCWG Meeting
Scheduled for October 13, 2010.
2011 meetings will be scheduled for the first Wednesday of each month unless the first day of the month is a Thursday. When this occurs, the meeting will be held the last Wednesday of the previous month.
This will provide a minimum of one week between PDCWG meetings and ROS meetings if ROS maintains the same schedule.