| NOGRR Number | 045 | NOGRR Title | Synchronization of OGRR219, Time Error Correction |
| --- | --- | --- | --- |
| Timeline | Normal | Action | Approved |
| Date of Decision |  | October 7, 2010 |  |
| Effective Date |  | Upon Texas Nodal Market implementation. |  |
| Priority and Rank Assigned |  | Not applicable. |  |
| Guide Section Requiring Revision |  | 2.2.9.1, Time Error |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) synchronizes the Nodal Operating Guides with Operating Guide Revision Request (OGRR) 219, Time Error Correction, which removes the requirement that ERCOT perform time error corrections for accumulated time errors exceeding five seconds. |  |
| Reason for Revision |  | Synchronizes the Nodal Operating Guides with Operating Guide Revision Request OGRR219. |  |
| Overall Market Benefit |  | Synchronized guides. |  |
| Overall Market Impact |  | None. |  |
| Consumer Impact |  | None. |  |
| Procedural History |  | - On 6/10/10, NOGRR045, the CEO Revision Request Review, and Impact Analysis were posted. - On 7/21/10, the Operations Working Group (OWG) considered NOGRR045. - On 8/18/10, OWG considered the 7/21/10 OWG Recommendation Report and Impact Analysis for NOGRR045. - On 9/16/10, ROS considered NOGRR045. - On 10/7/10, TAC considered NOGRR045. |  |
| OWG Decision |  | On 7/21/10, OWG was in consensus to recommend approval of NOGRR045 as revised by OWG. On 8/18/10, OWG was in consensus to endorse and forward the 7/21/10 OWG Recommendation Report and the Impact Analysis for NOGRR045 to ROS. |  |
| Summary of OWG Discussion |  | On 7/21/10, there was discussion regarding the overlap of Section 2.2.9.1 in NOGRR045 and NOGRR041, Synchronization of Section 2 with Nodal Protocols. OWG was in consensus to incorporate the revisions proposed to Section 2.2.9.1 by NOGRR041 into NOGRR045, thereby removing Section 2.2.9.1 completely from NOGRR041. On 8/18/10, there was no discussion. |  |
| ROS Decision |  | On 9/16/10, ROS unanimously voted to recommend approval of NOGRR045 as recommended by OWG in the 8/18/10 OWG Report. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 9/16/10, there was no discussion. |  |
| TAC Decision |  | On 10/7/10, TAC unanimously voted to approve NOGRR045 as recommended by ROS in the 9/16/10 ROS Report. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 10/7/10, there was no discussion. |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Synchronized guides. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | John Dumas/Sandip Sharma |
| E-mail Address | jdumas@ercot.com/ssharma@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3195/512-248-4298 |
| Cell Number |  |
| Market Segment | N/A. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sandra Tindall |
| E-Mail Address | stindall@ercot.com |
| Phone Number | 512-248-3867 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Proposed Guide Language Revision

2.2.9.1	Time Error

Sustained frequency deviations from scheduled frequency result in Time Error.  Time Error will be monitored and controlled in ERCOT as follows:

(1)	Time Error Monitoring - ERCOT will monitor accumulated Time Error and initiate time corrections.  The instantaneous Time Error is available to all QSEs on the MIS Public Area.  When Time Error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction.  The correction may end when the error is less than ±0.5 seconds, or when system events mandate termination.  The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction.

(2)	Time Error Correction - When a time correction is necessary, ERCOT will adjust scheduled frequency by arranging for more or less Resources by implementing a frequency offset.  Information will be communicated via hotline call to all QSEs, which will include the frequency offset (-.02 Hz for fast and +.02 Hz for slow) and the start time.  A time correction may be terminated after five hours, or after any hour without a 0.5 second error reduction.  ERCOT will provide adequate notice of the ending of a time correction to all QSEs in the ERCOT Region.