| NOGRR Number | 053 | NOGRR Title | Synchronization with OGRR226, Generation Resource Response Time Requirement |  |
| --- | --- | --- | --- | --- |
| Timeline | Urgent | Action |  | Approved |
| Date of Decision |  | October 7, 2010 |  |  |
| Effective Date |  | Upon the Nodal Protocol Transition Plan’s Texas Nodal Market Implementation Date as prescribed by zonal Operating Guide Section 1.3.7, Process for Transition to Nodal Operating Guide Sections. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Guide Section Requiring Revision |  | 2.2.10, Generation Resource Response Time Requirements (new) |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) aligns the Nodal Operating Guides with the zonal Operating Guides by adding language specified for Resource response times for certain directed and automatic actions. |  |  |
| Reason for Revision |  | To synchronize the Nodal Operating Guides with changes proposed in Operating Guide Revision Request (OGRR) 226, clarifying certain design and operating expectations for Resources. |  |  |
| Overall Market Benefit |  | Provides clarity to Resource Entities and insures ERCOT and Transmission Service Providers (TSPs) will know the time frames for execution of valid Dispatch Instructions. |  |  |
| Overall Market Impact |  | Improves reliability. |  |  |
| Consumer Impact |  | None. |  |  |
| Procedural History |  | - On 9/15/10, NOGRR053 and the associated CEO Revision Request Review were posted. - On 9/16/10, ROS considered NOGRR053. - On 9/30/10, an Impact Analysis was posted. - On 10/7/10, TAC considered NOGRR053. |  |  |
| ROS Decision |  | On 9/16/10, ROS voted to grant NOGRR053 Urgent status. There was one opposing vote from the Independent Retail Electric Provider (IREP) Market Segment. ROS then voted to recommend approval of NOGRR053 as submitted. There was one opposing vote from the IREP Market Segment. All Market Segments were present for the votes. |  |  |
| Summary of ROS Discussion |  | On 9/16/10, there was discussion regarding the urgency of NOGRR053. It was noted that NOGRR053 is a synchronization NOGRR and that the ERCOT CEO has determined that NOGRR053 is necessary prior to the Texas Nodal Market Implementation Date so that there are no gaps transitioning from the zonal Operating Guides to the Nodal Operating Guides. |  |  |
| TAC Decision |  | On 10/7/10, TAC unanimously voted to approve NOGRR053 as recommended by ROS in the 9/16/10 ROS Report. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 10/7/10, there was no discussion. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | . |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Additional equipment and controls. | Small additional cost for new Resources. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Improved reliability. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Frank Owens on behalf of the Operations Working Group (OWG) |
| E-mail Address | fowens@TEXASMPA.ORG |
| Company | Texas Municipal Power Agency |
| Phone Number | 936-873-1120 |
| Cell Number | 979-204-7725 |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sonja B. Mingo |
| E-Mail Address | smingo@ercot.com |
| Phone Number | 512.248-6463 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Proposed Guide Language Revision

- 2.2.10 	 Generation Resource Response Time Requirements

(1) 	All Generation Resources providing Voltage Support Service (VSS) as described in Protocol Section 3.15, Voltage Support, shall maintain the necessary procedures and processes plus communications, telemetry, remote control, automation, and staffing in order to normally comply with the response times listed below when a VSS Dispatch Instruction as described in Protocol Section 6.5.7.7 , Voltage Support Service, is given to the Generation Resource or the QSE representing a Generation Resource.  Compliance is based upon normal operating conditions where VSS Dispatch Instructions respect all equipment operating limits and other restrictions that are periodically placed on equipment.  The response time to a Dispatch Instruction shall commence with the successful receipt by the appropriate Entity.

(2)	In a Force Majeure Event, compliance with VSS Dispatch Instructions shall not be required.  TSPs and QSEs shall follow Dispatch Instructions for VSS except under those exemptions described in paragraphs (1) and (2) of Protocol Section 6.5.7.9, Compliance with Dispatch Instructions.

(3)	The required VSS response times for Generation Resources are:

(a)	For automatically switchable static VAR capable devices, when voltage or reactive measurements at the point of interconnection are outside of the limits as specified in paragraph (d) of Protocol Section 3.15.2, TSP and DSP Responsibilities  Related to Voltage Support; then the response (within the operating Reactive Power capability  of the Generation Resource) must be sufficient to initiate response in no more than one minute and return the measurement within the required range in no more than five minutes.

(b)	Response to a VSS Dispatch Instructions from ERCOT or authorized VSS Dispatch Instructions from a TSP, within the Reactive Power capability of the Generation Resource shall be completed in no more than five minutes of the receipt of a Dispatch Instruction.

(4) 	Shutting down and disconnecting Generation Resources from the ERCOT Transmission Grid:

(a)	On-Line Generation Resources must be able to commence their shutdown sequence within five minutes of receipt of a Dispatch Instruction from ERCOT.  Nuclear-fueled Generation Resources shall comply with the procedural requirements of the Nuclear Regulatory Commission (NRC) when receiving Dispatch Instructions from ERCOT to disconnect the Generation Resource from the ERCOT Transmission Grid.

(b)	If the ERCOT Transmission Grid condition requires breaker or switch operations needed to disconnect a non-MW producing generator  from the system  shall be completed as soon as practical, but no longer than 15 minutes of the receipt of a Dispatch Instruction from ERCOT.  Once disconnected from the ERCOT Transmission Grid, a Generation Resource shall complete as soon as practical, but no longer than 15 minutes, the required switching to return the system to a normal configuration except for Nuclear-fueled Generation Resources which shall comply with the procedural requirements of the NRC when receiving Dispatch Instructions from ERCOT to disconnect the Generation Resource from the ERCOT Transmission Grid.