## Slide 1: Analysis for the Determination of X, Y, and Z for Compliance Monitoring
ERCOT, September 30, 2010

## Slide 2: Review of X, Y, and Z
Nodal Protocol 8.1.1.4.1(10) states:
  “The GREDP/CLREDP performance criteria in paragraphs (7) through (9) above shall be reviewed and set by the TAC two months before the Texas Nodal Market Implementation Date (TNMID). The performance criteria will be subject to review by TAC beginning two months after the TNMID and as deemed necessary.”
X, Y, and Z are parameters which are used to determine how a Resource or DSR Portfolio performed for a given 5 minute interval
Generation Resource Energy Deployment Performance (GREDP) is a measure used for Generation Resources and DSR Portfolios
Controllable Load Resource Energy Deployment Performance (CLREDP) is a measure used for Controllable Load Resources
GREDP and CLREDP are measured in both % and MW.

## Slide 3: Review of X, Y, and Z cont.
Non-IRR Generation Resources, DSR Portfolios, and Controllable Load Resources must have a:
  GREDP/CLREDP less than the greater of X% or Y MW for 85% of the five-minute clock intervals in the month during which GREDP/CLREDP was calculated
Intermittent Renewable Resources (IRRs) must have a:
  GREDP less than Z% or the net MW output must be less than the expected MW output for 95% of the five-minute clock intervals in the month during which GREDP was calculated
  For IRRs, GREDP is only considered when the IRR has been curtailed
Further details about GREDP/CLREDP can be found in 8.1.1.4.1 of the Nodal Protocols

## Slide 4: Overview of Analysis for X, Y, and Z
For the purposes of the following analysis, ERCOT used data from the two 24-hour, the 40-Hour, and the 48-Hour Full-System Market and Reliability tests
For Non-IRR Resources, the analysis captures:
  The number of Resources that did not meet the X% or Y MW criteria for 85% of the intervals for which GREDP was calculated during the various LFC tests
For IRRs, the analysis captures:
  The number of Resources that did not meet the Z% or observed output <= expected output criteria during 95% of the intervals in which GREDP was calculated during the various LFC tests
For compliance monitoring, GREDP is actually scored over the course of a month
  Resource performance is likely to improve as more intervals are included in the scoring
For reference, average hourly CPS1 scores during the tests were:
24-Hour Test (8-4 to 8-5) | 24-Hour Test (8-19 to 8-20) | 40-Hour Test | 48-Hour Test
129 | 137 | 146 | 156

## Slide 5: Z% for IRR Compliance Monitoring
The value is currently set to 10%
Changes in Z don’t appear to greatly affect the number of failing Resources
  A majority of the passing IRRs appear to be meeting the Generation <= Expected MW for the purpose of passing any individual interval
Don’t see a reason to change Z at this point, but may be able to decrease the value (tighten the requirement) following further analysis after Go-Live
Test | Average Percent of Total Generation from WGRs
24- Hour (1) | 2.56%
24- Hour (2) | 7.69%
40-Hour | 1.65%
48-Hour | 4.35%
Note: The 2nd 24-Hour test was the only test during which a significant number of WGRs being curtailed.

## Slide 6: X% and Y MW for Non-IRR Compliance Monitoring (1st 24-Hour Test)
CPS1 performance during this test was 129
Using X = 5% and Y = 5 MW, 48 Resources did not meet the GREDP criteria at least 85% of the intervals
After between 5 and 7 for both X and Y, the amount of Resources failing begins to change less drastically
 |  | X (%) |  |  |  |  |  |  |  | 
 |  | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Y (MW) | 4 | 62 | 59 | 54 | 52 | 49 | 46 | 42 | 42 | 40
 | 4.5 | 60 | 57 | 53 | 51 | 48 | 45 | 41 | 41 | 39
 | 5 | 55 | 51 | 48 | 46 | 42 | 40 | 36 | 36 | 34
 | 5.5 | 52 | 49 | 46 | 44 | 40 | 38 | 34 | 34 | 32
 | 6 | 49 | 46 | 43 | 41 | 38 | 36 | 32 | 31 | 30
 | 6.5 | 45 | 43 | 40 | 38 | 34 | 33 | 30 | 30 | 29
 | 7 | 44 | 43 | 40 | 37 | 34 | 33 | 30 | 30 | 29
 | 7.5 | 41 | 40 | 37 | 35 | 32 | 31 | 29 | 29 | 28
 | 8 | 41 | 40 | 37 | 35 | 32 | 31 | 29 | 29 | 28

## Slide 7: X% and Y MW for Non-IRR Compliance Monitoring (2nd 24-Hour Test)
CPS1 performance during this test was 137
Using X = 5% and Y = 5 MW, 24 Resources did not meet the GREDP criteria at least 85% of the intervals
After between 5 and 6 for both X and Y, the amount of Resources failing begins to change less drastically
 |  | X (%) |  |  |  |  |  |  |  | 
 |  | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Y (MW) | 4 | 36 | 34 | 29 | 27 | 27 | 25 | 23 | 19 | 19
 | 4.5 | 29 | 28 | 24 | 22 | 22 | 20 | 18 | 16 | 15
 | 5 | 29 | 28 | 24 | 22 | 22 | 19 | 18 | 15 | 15
 | 5.5 | 27 | 26 | 21 | 20 | 18 | 17 | 16 | 14 | 14
 | 6 | 23 | 21 | 17 | 16 | 16 | 15 | 15 | 13 | 13
 | 6.5 | 22 | 21 | 16 | 16 | 16 | 15 | 15 | 13 | 13
 | 7 | 20 | 19 | 15 | 15 | 15 | 14 | 14 | 12 | 12
 | 7.5 | 19 | 17 | 14 | 14 | 14 | 13 | 13 | 11 | 11
 | 8 | 19 | 17 | 14 | 14 | 14 | 13 | 13 | 11 | 11

## Slide 8: X% and Y MW for Non-IRR Compliance Monitoring (40-Hour Test)
CPS1 performance during this test was 146
Using X = 5% and Y = 5 MW, 27 Resources did not meet the GREDP criteria at least 85% of the intervals
After between 5 and 7 for both X and Y, the amount of Resources failing begins to change less drastically
 |  | X (%) |  |  |  |  |  |  |  | 
 |  | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Y (MW) | 4 | 35 | 33 | 31 | 28 | 26 | 26 | 22 | 20 | 19
 | 4.5 | 33 | 31 | 29 | 25 | 24 | 24 | 21 | 19 | 19
 | 5 | 33 | 31 | 27 | 25 | 24 | 24 | 20 | 19 | 19
 | 5.5 | 31 | 28 | 25 | 24 | 23 | 22 | 19 | 18 | 18
 | 6 | 30 | 28 | 25 | 22 | 22 | 22 | 19 | 17 | 17
 | 6.5 | 27 | 25 | 23 | 21 | 21 | 21 | 18 | 17 | 17
 | 7 | 26 | 24 | 22 | 21 | 21 | 21 | 18 | 17 | 17
 | 7.5 | 24 | 23 | 21 | 20 | 20 | 20 | 16 | 16 | 16
 | 8 | 24 | 23 | 21 | 20 | 20 | 20 | 16 | 16 | 16

## Slide 9: X% and Y MW for Non-IRR Compliance Monitoring (48-Hour Test)
CPS1 performance during this test was 156
Using X = 5% and Y = 5 MW, 22 Resources did not meet the GREDP criteria at least 85% of the intervals
After between 5 and 7 for both X and Y, the amount of Resources failing begins to change less drastically
 |  | X (%) |  |  |  |  |  |  |  | 
 |  | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Y (MW) | 4 | 29 | 29 | 26 | 25 | 24 | 22 | 20 | 20 | 19
 | 4.5 | 28 | 28 | 25 | 23 | 22 | 21 | 19 | 19 | 19
 | 5 | 26 | 26 | 22 | 21 | 19 | 18 | 16 | 16 | 16
 | 5.5 | 24 | 24 | 22 | 21 | 19 | 18 | 16 | 16 | 16
 | 6 | 23 | 23 | 20 | 20 | 19 | 18 | 16 | 16 | 16
 | 6.5 | 21 | 21 | 18 | 18 | 18 | 17 | 15 | 15 | 15
 | 7 | 20 | 20 | 17 | 17 | 17 | 17 | 15 | 15 | 15
 | 7.5 | 19 | 19 | 16 | 16 | 16 | 16 | 14 | 14 | 13
 | 8 | 18 | 18 | 15 | 15 | 15 | 15 | 12 | 12 | 12

## Slide 10: X% and Y MW for Non-IRR Compliance Monitoring (48-Hour Test: Hours Ending 2-5)
CPS1 performance during these hours was 161
Using X = 5% and Y = 5 MW, 11 Resources did not meet the GREDP criteria at least 85% of the intervals
After between 5 and 6 for both X and Y, the amount of Resources failing begins to change less drastically
 |  | X (%) |  |  |  |  |  |  |  | 
 |  | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Y (MW) | 4 | 15 | 13 | 11 | 10 | 10 | 9 | 9 | 8 | 8
 | 4.5 | 15 | 13 | 11 | 10 | 10 | 9 | 9 | 8 | 8
 | 5 | 15 | 13 | 11 | 10 | 10 | 9 | 9 | 8 | 8
 | 5.5 | 14 | 12 | 10 | 9 | 9 | 8 | 8 | 7 | 7
 | 6 | 14 | 12 | 10 | 9 | 9 | 8 | 8 | 7 | 7
 | 6.5 | 13 | 11 | 9 | 8 | 8 | 7 | 7 | 6 | 6
 | 7 | 13 | 11 | 9 | 8 | 8 | 7 | 7 | 6 | 6
 | 7.5 | 12 | 10 | 8 | 7 | 7 | 6 | 6 | 5 | 5
 | 8 | 12 | 10 | 8 | 7 | 7 | 6 | 6 | 5 | 5

## Slide 11: X% and Y MW for Non-IRR Compliance Monitoring (48-Hour Test: Hours Ending 6-14)
CPS1 performance during these hours was 148
Using X = 5% and Y = 5 MW, 35 Resources did not meet the GREDP criteria at least 85% of the intervals
After between 5 and 7 for both X and Y, amount of Resources failing begins to change less drastically
 |  | X (%) |  |  |  |  |  |  |  | 
 |  | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Y (MW) | 4 | 41 | 41 | 40 | 40 | 36 | 34 | 34 | 33 | 32
 | 4.5 | 39 | 39 | 38 | 38 | 34 | 32 | 32 | 31 | 31
 | 5 | 36 | 36 | 35 | 35 | 31 | 29 | 29 | 28 | 28
 | 5.5 | 35 | 35 | 35 | 35 | 31 | 29 | 29 | 28 | 28
 | 6 | 34 | 34 | 34 | 34 | 30 | 28 | 28 | 27 | 27
 | 6.5 | 34 | 34 | 34 | 34 | 30 | 28 | 28 | 27 | 27
 | 7 | 33 | 33 | 33 | 33 | 30 | 28 | 28 | 27 | 27
 | 7.5 | 31 | 31 | 31 | 31 | 28 | 26 | 26 | 25 | 25
 | 8 | 29 | 29 | 29 | 28 | 26 | 24 | 24 | 23 | 22

## Slide 12: X% and Y MW for Non-IRR Compliance Monitoring (48-Hour Test: Hours Ending 15-21)
CPS1 performance during these hours was 172
Using X = 5% and Y = 5 MW, 15 Resources did not meet the GREDP criteria at least 85% of the intervals
After between 5 and 6 for both X and Y, amount of Resources failing begins to change less drastically
 |  | X (%) |  |  |  |  |  |  |  | 
 |  | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Y (MW) | 4 | 25 | 23 | 18 | 17 | 14 | 14 | 14 | 14 | 13
 | 4.5 | 22 | 21 | 16 | 15 | 13 | 13 | 13 | 13 | 13
 | 5 | 19 | 19 | 15 | 14 | 12 | 12 | 12 | 12 | 12
 | 5.5 | 18 | 18 | 15 | 14 | 12 | 12 | 12 | 12 | 12
 | 6 | 18 | 18 | 15 | 14 | 12 | 12 | 12 | 12 | 12
 | 6.5 | 16 | 16 | 13 | 12 | 11 | 11 | 11 | 11 | 11
 | 7 | 16 | 16 | 13 | 12 | 11 | 11 | 11 | 11 | 11
 | 7.5 | 16 | 15 | 13 | 12 | 11 | 11 | 11 | 11 | 11
 | 8 | 13 | 13 | 11 | 10 | 9 | 9 | 9 | 9 | 9

## Slide 13: X% and Y MW for Non-IRR Compliance Monitoring (48-Hour Test: Hours Ending 22-1)
CPS1 performance during these hours was 139
Using X = 5% and Y = 5 MW, 9 Resources did not meet the GREDP criteria at least 85% of the intervals
After between 5 and 6 for both X and Y, amount of Resources failing begins to change less drastically
 |  | X (%) |  |  |  |  |  |  |  | 
 |  | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Y (MW) | 4 | 16 | 15 | 12 | 11 | 10 | 8 | 8 | 7 | 7
 | 4.5 | 14 | 13 | 10 | 9 | 8 | 6 | 6 | 5 | 5
 | 5 | 13 | 12 | 9 | 8 | 7 | 5 | 5 | 4 | 4
 | 5.5 | 11 | 10 | 8 | 8 | 7 | 5 | 5 | 4 | 4
 | 6 | 11 | 10 | 8 | 8 | 7 | 5 | 5 | 4 | 4
 | 6.5 | 10 | 10 | 8 | 7 | 6 | 5 | 5 | 4 | 4
 | 7 | 9 | 8 | 6 | 6 | 5 | 4 | 4 | 4 | 4
 | 7.5 | 8 | 8 | 6 | 6 | 5 | 4 | 4 | 4 | 4
 | 8 | 8 | 8 | 6 | 6 | 5 | 4 | 4 | 4 | 4

## Slide 14: Conclusions
Control has continued to improve throughout Phase 5 of Market Trials
  This can be observed both in the CPS1 scores and the GREDP performance for the individual Resources
There are still two Full-System Market and Reliability tests prior to Go-Live which will allow ERCOT and QSEs to continue to improve upon their performance
For Z, there does not appear to be an obvious need to change the existing value of 10%
  Z may even be able to be reduced following further analysis after Go-Live to tighten the criteria
For X and Y, there also does not appear to be an obvious need to change the existing values of 5% and 5 MW
  The number of Resources failing the GREDP criteria did not change drastically after around 5 or 7 for both X and Y
Due to the fact that compliance monitoring is actually done on a monthly basis, Resource performance is likely due to improve simply due to the increase in intervals on which performance is analyzed
  The longest period used for this analysis was 48 hours