| NOGRR Number | 044 | NOGRR Title | Clarification of a PSS In-Service |
| --- | --- | --- | --- |
| Timeline | Normal | Action | Tabled |
| Date of Decision |  | October 20, 2010 |  |
| Proposed Effective Date |  | To be determined. |  |
| Priority and Rank Assigned |  | To be determined. |  |
| Guide Section Requiring Revision |  | 2.2.6, Power System Stabilizers |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) clarifies that a Power System Stabilizer (PSS) must be “On” and in an active MW range to be considered in service. This NOGRR also updates the specific dates of PSS installation from 2008 to 2011. |  |
| Reason for Revision |  | It is currently perceived that a PSS is in service when a generator is On-Line and synchronized to the ERCOT Transmission Grid. A PSS can be turned on or off via a simple control switch. However, if the PSS is turned on, the PSS does not become active or responsive until the MW level surpasses the unit stability limit as it increases in MWs from zero MWs after synchronization to the ERCOT Transmission Grid and in the decreasing MW mode it will de-activate when it surpasses the defined low stability limit while synchronized to the ERCOT Transmission Grid. The latter is usually when the unit is about to come Off-Line. The requirement in paragraphs (2), (3), and (4) of Section 2.2.6 with a date of 2008 was in anticipation of an earlier Texas Nodal Market Implementation Date. This NOGRR revises the date to reflect the updated Texas Nodal Market Implementation Date and to remove any retroactive date requirements. |  |
| Overall Market Benefit |  | No monetary benefit. However, a better clarity as to the actual PSS serviceable range. |  |
| Overall Market Impact |  | None. |  |
| Consumer Impact |  | None. |  |
| Procedural History |  | - On 6/3/10, NOGRR044 and the associated CEO Revision Request Review were posted. - On 7/19/10, ERCOT comments were posted. - On 7/21/10, the Operations Working Group (OWG) considered NOGRR044. - On 8/2/10, an Impact Analysis was posted. - On 8/18/10, the OWG considered the 7/21/10 OWG Recommendation Report and Impact Analysis for NOGRR044. - On 9/23/10, OWG again considered NOGRR044. - On 10/20/10, OWG again considered NOGRR044. |  |
| OWG Decision |  | On 7/21/10, OWG was in consensus to recommend approval of NOGRR044 as amended by the 7/19/10 ERCOT comments and as revised by OWG. On 8/18/10, OWG was in consensus to table NOGRR044 for one month. On 9/23/10, OWG was in consensus to table NOGRR044 for one month. On 10/20/10, OWG was in consensus to table NOGRR044 for one month. |  |
| Summary of OWG Discussion |  | On 7/21/10, ERCOT Staff recommended the addition of changes proposed in Section 2.2.6 by NOGRR041, Synchronization of Section 2 with Nodal Protocols, to NOGRR044. On 8/18/10, it was requested that NOGRR044 be tabled for one month to allow time for manufacturers to review and comment. On 9/23/10, it was requested that NOGRR044 be tabled for one month to allow time for PSS vendors to review and comment. On 10/20/10, it was requested that NOGRR044 be tabled for one month to allow time for PSS vendors to review and comment. |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None | None |
|  | 2 |  | 1.5 Full Time Equivalent (FTE) each for six Transmission and/or Distribution Service Providers (TDSPs) @ $65/hour |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Clarification of actual PSS engagement. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Jack Thormahlen |
| E-mail Address | Jack.thormahlen@lcra.org |
| Company | LCRA |
| Phone Number | 512-473-3200 ext 2635 |
| Cell Number |  |
| Market Segment | Cooperative |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 071910 | Proposed language changes to retain the 2008 dividing date for Generation Resources’ obligations with respect to PSS equipment and other clarifications. |

Proposed Guide Language Revision

2.2.6	Power System Stabilizers

- Generation Resources with  Power System Stabilizers (PSSs) shall keep their PSSs in-service (“On” or energized) at all times the generator is synchronized to the ERCOT Transmission Grid.

- Generation Entities shall notify their QSEs of any change in PSS status and when the PSS returns to normal operation.  QSEs shall notify ERCOT of any change in PSS status and when the PSS returns to normal operation and shall supply PSS status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.  ERCOT shall notify the appropriate TO of a change in PSS status and when the PSS returns to normal operation.

- Synchronous Generation Resources greater than 10 MW installed between January 1, 2008 and the Texas Nodal Market Implementation Date shall install a PSS and place the PSS in service within 180 days after the Texas Nodal Market Implementation Date.  Synchronous Generation Resources greater than 10MW installed after the Texas Nodal Market Implementation Date shall install a PSS and place the PSS in-service prior to the commercial operation start date of the Generation Resource.  The Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- Synchronous Generation Resources greater than 10 MW installed before January 1, 2008 are subject to the following requirements:

(a)	All Generation Resources that are in this category shall notify ERCOT:

(i)	Whether or not a PSS has been installed; and

(ii)	Whether or not PSS settings have been determined and the PSS has been 	or will be placed in-service.

(b)	If the PSS has been or will be placed in-service, the Generation Resource will provide the stabilizer settings to ERCOT and the TSP within 30 days of the PSS in-service date.

(c)	If a PSS was in-service prior to January 1, 2008 the PSS must remain in-service with the established PSS settings, provided that ERCOT may direct the Generation Resource  to modify the settings.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.

(d)	If a PSS is installed and in-service and the conditions in item (b) above do not apply, a Generation Resource may establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.

(e)

If a PSS has been installed but has not been placed in-service, ERCOT may  assess the need to have such PSS brought in-service and communicate the assessment to the Generation Resource.  Within 180 days of the ERCOT determination to have such PSS brought in-service, the Generation Resource shall establish PSS settings to dampen modes with oscillations within the range specified by ERCOT and place the PSS in-service.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of  the PSS in-service date.

- If an excitation system on a synchronous Generation Resource greater than 10 MW is modified or replaced after January 1, 2008, the Generation Resource shall install a PSS, establish PSS settings to dampen modes with oscillations within the range of 0.2 to 2.0 Hz, and place the PSS in-service.  The settings shall be tested and tuned for adequate damping to ensure the excitation system has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- If it is determined that a change in PSS settings or the addition of a PSS to a synchronous Generation Resource would improve overall system performance, ERCOT shall coordinate with the Generation Resource owner to determine appropriate settings.  Within 180 days of determining appropriate settings, the Generation Resource owner shall revise the PSS setting and/or install the PSS.  Any PSS setting established pursuant to this section shall be established to dampen modes with oscillations as directed by ERCOT and place the PSS in-service.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- At least every five years, Generation Entities shall conduct performance tests on PSS settings or verify PSS performance based on operational data.  If PSS equipment characteristics are modified, the Generation Entity shall conduct a performance test within 30 days of the modification.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date

- The results of PSS tests or PSS performance verification shall be supplied to ERCOT and the TSP within 30 days of a request from ERCOT.