## Slide 1: 2010 LOLE Study – Methodology and Results
Dan Woodfin
Director, System Planning
TAC
11/04/2010

## Slide 2: Overview
The scope of this study is to evaluate the impact of system volatility on the relationship between generation reserve levels and system reliability.
The following components of system volatility are being considered:
  The forced outage and derating of generating facilities.
  Load forecast uncertainty related to weather.
  The intermittent nature of wind power.
The main indicator of reliability is the Loss-of-Load Events (LOLEV).
  LOLEV is the number of times in a year that available generation was incapable of meeting demand
  Traditional one-day-in-10-years criteria is equivalent to 0.1 LOLEV
Study year was 2012

## Slide 3: Input Data
Generation (non-wind)
  Existing and signed IA generation
    Includes generation and load from private use networks
    Does not include DC ties or hydroelectric capacity.
    Seasonal capacity ratings from RARF
    Forced outage rates from NERC GADS
      Individual unit data, if available
      Regional averages for unit size and vintage, if not
Load
  Five load scenarios
    Extreme summer (10% probability of occurrence)
    Warmer than average (23%)
    Average (34%)
    Cooler than average (23%)
    Much cooler than average (10%)
  Specific historic year’s hourly chronological load used for each scenario, chosen to be statistically representative

## Slide 4: Input Data, continued
Wind Generation
  Based on the annual wind generation patterns prepared for ERCOT by AWS Truewind for the CREZ analysis.
    Typical, hourly pattern for each of ~1000 geographically-dispersed 100MW sites
    Patterns derived to have representative hourly volatility
  One or more patterns chosen for each existing wind plant and scaled to size of plant
  When evaluating a particular day in one of the load scenarios, the hourly wind profile for that day was chosen from these patterns for dates ±7 days from date under study
  Forced outages of individual wind turbines are not being modeled.

## Slide 5: Generator outage modeling
Outages are modeled sequentially, using random draws from two exponential distributions.
  The time on outage for each unit is randomly drawn from an exponential distribution with mean equal to the mean time to repair (MTTR):
    MTTR = (FOH + EFDH) / # of FO occurrences
  The time in service for each unit is randomly drawn from an exponential distribution with mean equal to the mean time to failure (MTTF):
    MTTF = SOAF x MTTR x [(1/ EFORd) – 1 )]
    SOAF is the scheduled outage adjustment factor equal to [(8784 – SOH) / 8784] which is applied while calculating MTTF to account for any loss of outage time due to overlap of forced outages with scheduled outages.
  The outage modeling described above results in unit unavailability due to forced outage equal to EFORd.

## Slide 6: Flowchart
For every unit, build sequences of generator availability and unavailability periods using MTTF and MTTR respectively.
For every day, create random daily wind profiles. To randomly choose a day’s wind profile, a span of +/- 7 days is used.
Generate hourly resource profiles by summing up the hourly capacity available (wind and non-wind).
Once hourly resource profiles are available, the margin is calculated.
A negative margin indicates a loss of load hour and it’s value the amount of load that could not be served. A sequence of loss of load hours is treated as one loss of load event.
The reliability metrics (LOLEV, EUE and LOLH) are updated based on the hourly margin obtained.
Based on the probability associated with each of the load scenarios, calculate the study-wide reliability indices.
Once a (maximum) number of iterations has been run or the stopping criteria have been met, proceed to the next load scenario. See next slide for the stopping criteria.
Start
Read generation, wind and load data from an EXCEL file
Generate random outages and randomize available wind capacity for a pre-specified number of years
Proceed with the next load scenario
Update reliability metrics (LOLEV EUE, LOLH)
For every load scenario
Calculate probability based reliability indices
Print results
Stop
Check whether the stopping criteria are met
no
yes
Evaluate the hourly margin between resource and load (Margin = Resources – Demand)

## Slide 7: ELCC calculation
Methodology for the ELCC calculation:
  LOLEV is calculated, using process on previous slide, for the base case system with all generation, including wind
  Wind units are removed and LOLEV is calculated
  The capacity of each non-wind generator in the fleet is proportionally increased and the LOLEV is recalculated
    This process is repeated until the resulting LOLEV is equivalent to that in the base case
  The ELCC value is equal to the ratio of additional non-wind capacity (capacity multiplier-1 times the installed non-wind capacity) divided by the total installed capacity of wind, in percent
This ELCC calculation effectively “equalizes” the contribution to LOLEV from wind to that of the non-wind generation, on an annual basis

## Slide 8: Comparison to the 2007 study by Global Energy Decisions
2007 study suggested ELCC for wind of 8.7% and target reserve margin of 12.9% or 13.7% depending on comparison unit type
The current study differs from the 2007 study in the following ways:
  ERCOT used a family of load profiles representing different weather conditions.
  All hours of the year are being modeled instead of a representative week from each month.
  Generator outages are modeled sequentially.
  Wind volatility is modeled in a more dynamic way.
  The ELCC of existing wind is compared to the reliability of the existing fleet rather than hypothetical new generating unit.
  A much higher number of iterations was performed in order to ensure the statistical significance of the results.

## Slide 9: Study Results
The ELCC for wind using the LOLEV metric is 12.2%
The Target Reserve Margin using the LOLEV metric of 0.1 is 13.75%

## Slide 10
Questions?