ERCOT Nodal Protocols

Section 5: Transmission Security Analysis and Reliability Unit Commitment

Updated: November 1, 2010

(Effective upon the Nodal Protocol Transition Plan’s Texas Nodal Market Implementation Date as prescribed by zonal Protocol Section 21.12, Process for Transition to Nodal Market Protocol Sections)

5	Transmission Security Analysis and Reliability Unit Commitment (RUC)	5-1

5.1	Introduction	5-1

5.2	Reliability Unit Commitment Timeline Summary	5-2

5.2.1	RUC Normal Timeline Summary	5-2

5.2.2	RUC Process Timing Deviations	5-3

5.2.2.1	RUC Process Timeline After a Delay of the Day-Ahead Market	5-3

5.2.2.2	RUC Process Timeline After an Aborted Day-Ahead Market	5-3

5.3	ERCOT Security Sequence Responsibilities	5-5

5.4	QSE Security Sequence Responsibilities	5-6

5.5	Security Sequence, Including RUC	5-7

5.5.1	Security Sequence	5-7

5.5.2	Reliability Unit Commitment (RUC) Process	5-9

5.5.3	Communication of RUC Commitments and Decommitments	5-12

5.6	RUC Cost Eligibility	5-13

5.6.1	Verifiable Costs	5-13

5.6.1.1	Verifiable Startup Costs	5-17

5.6.1.2	Verifiable Minimum-Energy Costs	5-17

5.6.2	RUC Startup Cost Eligibility	5-17

5.6.3	Forced Outage of a RUC-Committed Resource	5-18

5.6.4	Cancellation of a RUC Commitment	5-19

5.7	Settlement for RUC Process	5-19

5.7.1	RUC Make-Whole Payment	5-19

5.7.1.1	RUC Guarantee	5-21

5.7.1.2	RUC Minimum-Energy Revenue	5-23

5.7.1.3	Revenue Less Cost Above LSL During RUC-Committed Hours	5-24

5.7.1.4	Revenue Less Cost During QSE Clawback Intervals	5-26

5.7.2	RUC Clawback Charge	5-28

5.7.2	RUC Clawback Charge	5-30

5.7.3	Payment When ERCOT Decommits a QSE-Committed Resource	5-33

5.7.4	RUC Make-Whole Charges	5-35

5.7.4.1	RUC Capacity-Short Charge	5-36

5.7.4.1.1	Capacity Shortfall Ratio Share	5-37

5.7.4.1.2	RUC Capacity Credit	5-41

5.7.4.2	RUC Make-Whole Uplift Charge	5-41

5.7.5	RUC Clawback Payment	5-42

5.7.6	RUC Decommitment Charge	5-43

# Transmission Security Analysis and Reliability Unit Commitment (RUC)

5.1	Introduction

(1)	Transmission security analysis and Reliability Unit Commitment (RUC) are used to ensure ERCOT System reliability and to ensure that enough Resource capacity, in addition to Ancillary Service capacity, is committed in the right locations to reliably serve the forecasted Load on the ERCOT System.

(2)	ERCOT shall conduct at least one Day-Ahead RUC (DRUC) and at least one Hourly RUC (HRUC) before each hour of the Operating Day.  ERCOT, in its sole discretion, may conduct a RUC at any time to evaluate and resolve reliability issues.

(3)	The DRUC must be run after the close of the Day-Ahead Market (DAM).

(4)	The DRUC uses Three-Part Supply Offers submitted before the DAM by Qualified Scheduling Entities (QSEs) that were considered in the DAM but not awarded in the DAM.  A QSE may not submit a Three-Part Supply Offer to be considered in the DRUC unless the offer was also submitted for consideration in the DAM.

(5)	ERCOT must initiate the HRUC process at least one hour before the Operating Hour to fine-tune the Resource commitments using updated Load forecasts and updated Outage information.

(6)	The RUC Study Period for DRUC is the next Operating Day.  The RUC Study Period for HRUC is the balance of the current Operating Day plus the next Operating Day if the DRUC for the Operating Day has been solved.

(7)	HRUC may decommit Resources only to maintain the reliability of the ERCOT System.

(8)	For each RUC Study Period, the RUC considers capacity requirements for each hour of the RUC Study Period with the objective of minimizing costs based on Three-Part Supply Offers and while substituting a proxy Energy Offer Curve for the Energy Offer Curve.  The proxy Energy Offer Curve is calculated in a way that minimizes the effect of the proxy Energy Offer Curves on optimization.

(9)	The calculated Resource commitments arising from each RUC process must be reviewed by ERCOT before issuing Dispatch Instructions to QSEs to commit, extend, or decommit Resources.

(10)	The Security Sequence is a set of prerequisite processes for RUC that describes the key system components and inputs that are required to support the RUC process, the RUC process itself, and the ERCOT review of the Resource commitment recommendations made by the RUC process.

(11)	The RUC process may not be used to buy Ancillary Service unless the Ancillary Service Offers submitted in the DAM are insufficient to meet the requirements of the Ancillary Service Plan.

(12)	After the use of market processes to the fullest extent practicable without jeopardizing the reliability of the ERCOT System, any ERCOT Dispatch Instructions for additional capacity that order a QSE to commit a specific Generation Resource to be On-Line shall be considered a RUC dispatch for the purpose of the Settlement of payments and charges related to the committed Generation Resource.  An Operating Condition Notice (OCN), Advisory, Watch, or Emergency Notice requesting the available capacity of any currently available Generation Resources but not naming specific Generation Resources is not considered a RUC dispatch for purposes of Settlement.

5.2	Reliability Unit Commitment Timeline Summary

- 5.2.1	RUC Normal Timeline Summary

The following Reliability Unit Commitment (RUC) Timeline Summary describes the normal timeline for RUC activities that occur in the Day-Ahead and Adjustment Periods.

- 5.2.2	RUC Process Timing Deviations

- 5.2.2.1	RUC Process Timeline After a Delay of the Day-Ahead Market

If the Day-Ahead Market (DAM) execution is delayed in accordance with Section 4.1.2, Day-Ahead Process and Timing Deviations, ERCOT shall conduct a Day-Ahead Reliability Unit Commitment (DRUC) after 1430 in the Day-Ahead and no earlier than one hour following the posting of DAM awards information on the Market Information System (MIS) Public Area as set forth in Section 4.5.3, Communicating DAM Results.  In this event, ERCOT will use the Current Operating Plan (COP) and Trades Snapshot taken just prior to the execution of the DRUC to settle RUC charges.

- 5.2.2.2	RUC Process Timeline After an Aborted Day-Ahead Market

(1)	If ERCOT aborts all or part of the Day Ahead process in accordance with Section 4.1.2, Day-Ahead Process and Timing Deviations, ERCOT shall use the following Supplemental Ancillary Services Market (SASM) process to purchase Ancillary Services for the next Operating Day and the Hourly Reliability Unit Commitment (HRUC) process described in this Section in lieu of the DRUC process.

(2)	When the DAM is aborted, ERCOT shall include in the Emergency Condition notice required by paragraph (2) of Section 4.1.2 the time when it intends to conduct the SASM described in this Section 5.2.2.2 to procure the amounts of Ancillary Services necessary to meet the Ancillary Service Plan for the Operating Day affected by the aborted DAM.  ERCOT shall allow at least one hour between the issuance of the Emergency Condition notice and the beginning of this SASM.

(3)	After the issuance of the Emergency Condition notice described in paragraph (2) above and prior to the beginning of this SASM, a Qualified Scheduling Entity (QSE) may cancel unexpired Ancillary Service Offers that were submitted for the aborted DAM.

(4)	A QSE may submit Ancillary Service Offers for this SASM after the issuance of the Emergency Condition notice described in paragraph (2) above and prior to the beginning of this SASM.  For this SASM, these QSE Ancillary Service Offers shall not be subject to the provisions of Section 6.4.8.2.1, Resubmitting Offers for Ancillary Services in the Adjustment Period.

(5)	For this SASM, the QSE must submit the Self-Arranged Ancillary Service Quantity for the next Operating Day in accordance with the timeline described in paragraph (8) below.  This amount may be different from the self-arrangement amounts previously submitted for the aborted DAM.

(6)	The amount of each Ancillary Service to be procured by ERCOT in this SASM is the amount of each Ancillary Service specified in the ERCOT Ancillary Service Plan posted prior to the aborted DAM less the total amount of each Ancillary Service in the QSE submittals for self arranged Ancillary Services for this SASM.

(7)	This SASM will settle in accordance with Section 6.7, Real-Time Settlement Calculations for the Ancillary Services.

(8)	The SASM process for acquiring Ancillary Services in the event of an aborted Day-Ahead process shall be conducted in accordance with Section 6.4.8.2.2, SASM Clearing Process, but shall use the following activities and timeline with time “X” being the time specified by ERCOT for the beginning of the SASM process in the Emergency Condition notice described above.

| SASM Process | QSE Activities: | ERCOT Activities: |
| --- | --- | --- |
| Time = X |  | The time specified in the Emergency Condition notice for the SASM to begin. |
| Time = X plus 30 minutes | Must complete submission of Self-Arranged Ancillary Service Quantities limited to the additional Ancillary Service Obligation of the QSE. | Determine the amount of Ancillary Services to be procured. |
| Time = X plus 35 minutes |  | Execute SASM. |
| Time = X plus 45 minutes |  | Notify QSEs with awards of results. Post the quantities and Market Clearing Prices for Capacity (MCPCs) of Ancillary Services bought in the SASM. |
| Time = X plus 60 minutes | Submit updated COP with updated Ancillary Service Resource Responsibility. | Validate COPs for Ancillary Service Resource Responsibility. |

(9)	As soon as practicable, but no later than the time specified above, ERCOT shall notify each QSE of its awarded Ancillary Service Offer quantities, specifying Resource, Ancillary Service type, SASM MCPC, and the first and last hours of the awarded offer.

(10)	As soon as practicable, but no later than the time specified above, ERCOT shall post on the MIS Public Area the hourly:

(a)	SASM MCPC for each type of Ancillary Service for each hour;

(b)	Total Ancillary Service procured in MW by Ancillary Service type for each hour; and

(c)	Aggregated Ancillary Service Offer Curve for each Ancillary Service for each hour.

(11)	No sooner than 1800 in the Day-Ahead and after the completion of the SASM process described in this Section 5.2.2.2, ERCOT shall execute an HRUC process.

(a)	The RUC Study Period for this HRUC process is the balance of the current Operating Day plus the next Operating Day.  This HRUC process may be a post-1800 HRUC for the current Operating Day.

(b)	The COP and Trades Snapshot taken just prior to the execution of the HRUC process described in this Section 5.2.2.2 will be used to settle RUC charges in the Operating Day affected by the aborted DAM.

(c)	This HRUC process described in this Section 5.2.2.2 may commit Resources to supply Ancillary Services if the Ancillary Service Offers submitted in the SASM described in this Section 5.2.2.2 are insufficient to meet the requirements of the Ancillary Services Plan in the Operating Day affected by the aborted DAM.

5.3	ERCOT Security Sequence Responsibilities

(1)	ERCOT shall start the Day-Ahead Reliability Unit Commitment (DRUC) process at 1430 in the Day Ahead.

(2)	For each DRUC, ERCOT shall use a snapshot of Resource commitments taken at 1430 in the Day Ahead to settle RUC charges.  For each HRUC, ERCOT shall use a snapshot of Resource commitments from each QSE’s most recently submitted COP before HRUC execution to settle RUC charges.

(3)	For each RUC process, ERCOT shall:

(a)	Execute the Security Sequence described in Section 5.5, Security Sequence, Including RUC, including:

(i)	Validating Three-Part Supply Offers, defined in Section 4.4.9.1, Three-Part Supply Offers; and

(ii)	Reviewing the Resource commitment recommendations made by the RUC algorithm; and

(b)	Post to the MIS Secure Area, the following information related to the RUC:

(i)	All active and binding transmission constraints (contingency and overloaded element pair information where available) used as inputs to RUC; and

(ii)	All Resources that were committed or decommitted by the RUC process; and

(c)	Issue Dispatch Instructions to notify each QSE of its Resource commitments or decommittments.

(4)	ERCOT shall provide each QSE with the information necessary to pre-validate their data for DRUC and HRUC including:

(a)	Publishing validation rules for offers, bids, and trades; and

(b)	Posting any software documentation and code that is not Protected Information to the MIS Secure Area within five Business Days of receipt by ERCOT.

5.4	QSE Security Sequence Responsibilities

During the Security Sequence, each Qualified Scheduling Entity (QSE) must:

(1)	Submit its Current Operating Plan (COP) and update its COP as required in Section 3.9, Current Operating Plan (COP);

(2)	Submit any Three-Part Supply Offers before:

(a)	1000 in the Day-Ahead for the Day-Ahead Market (DAM) and Day-Ahead Reliability Unit Commitment (DRUC) being run in that Day-Ahead, if the QSE wants the offer to be used in  those DAM and DRUC processes; and

(b)	The end of the Adjustment Period for each Hourly Reliability Unit Commitment (HRUC), if the QSE wants the offer to be used in the HRUC process;

(3)	Submit any Capacity Trades before 1430 in the Day-Ahead for the DRUC and before the end of the Adjustment Period for each HRUC, if the QSE wants those Capacity Trades included in the calculation of RUC settlement;

(4)	Submit any Energy Trades before 1430 in the Day-Ahead for the DRUC and by the end of the Adjustment Period for each HRUC; if the QSE wants those Energy Trades included in the calculation of RUC Settlement;

(5)	Submit an updated COP before 1430 in the Day-Ahead that shows the specific Resources that will be used to supply the QSE’s Ancillary Service Supply Responsibility; and

(6)	Acknowledge receipt of Resource commitment or decommitment Dispatch Instructions by submitting an updated COP.

5.5	Security Sequence, Including RUC

5.5.1	Security Sequence

(1)	The figure below highlights the key computational modules and processes that are used in the Security Sequence:

(2)	The Security Sequence uses computational modules functionally similar to those used in Real-Time Sequence, however, the inputs into the Security Sequence are based on a snapshot of projected hourly system conditions and constraints rather than Real-Time data.

(3)	The Security Sequence uses the status of all transmission breakers and switches (current status for the first hour and normal status for all other hours of Hourly Reliability Unit Commitment (HRUC) and normal status for all hours of Day-Ahead Reliability Unit Commitment (DRUC)), updated for approved Planned Outages for equipment out of service and returned to service for building a representation of the ERCOT Transmission Grid for each hour of the Reliability Unit Commitment (RUC) Study Period.  The Network Topology Processor constructs a network model for each hour that must be used by the Bus Load Forecast to estimate the hourly Load for each transmission bus.

(4)	The weather forecast obtained by ERCOT must be provided to the Dynamic Rating Processor to create weather-adjusted MVA limits for each hour of the RUC Study Period for all transmission lines and transformers that have Dynamic Ratings.

(5)	ERCOT shall analyze base configuration, select n-1 contingencies and select n-2 contingencies under the Operating Guides.  The Operating Guides must also specify the criteria by which ERCOT may remove contingencies from the list.  ERCOT shall post to the Market Information System (MIS) Secure Area the standard contingency list, including identification of changes from previous versions before being used in the Security Sequence.  ERCOT shall evaluate the need for Resource-specific deployments during Real-Time operations for management of congestion consistent with the Operating Guides.

(6)	ERCOT shall also post to the MIS Secure Area any contingencies temporarily removed from the standard contingency list by ERCOT immediately after successful execution of the Security Sequence.  ERCOT shall include the reason for removal of any contingency as soon as practicable but not later than one hour after removal.

(7)	As part of the Network Security Analysis (NSA), for each hour of the RUC Study Period, ERCOT shall analyze all selected contingencies and perform the following:

(a)	Perform full AC analysis of all contingencies;

(b)	Monitor element and bus voltage limit violations; and

(c)	Monitor transmission line and transformer security violations.

(8)	As part of the NSA, if there is an approved Remedial Action Plan (RAP) available, it must be used before considering a Resource commitment.

(9)	ERCOT shall review all security violations prior to RUC execution.

(10)	ERCOT shall model all approved Special Protection Systems (SPSs) and RAPs in the contingency analysis.  The computational modules must enable ERCOT to analyze contingencies, including the effects of all approved automatically deployed SPSs.

(11)	ERCOT may deselect certain contingencies known to cause errors or that otherwise result in inconclusive study output in the RUC.  On continued de-selection of contingencies, ERCOT shall prepare an analysis to determine the cause of the error.  ERCOT may use information from the Day-Ahead processes as decision support during the Hour-Ahead processes.  ERCOT shall post to the MIS Secure Area any contingencies deselected by ERCOT and must include the reason for removal as soon as practicable, but not later than one hour after deselection.

5.5.2	Reliability Unit Commitment (RUC) Process

(1)	The RUC process recommends commitment of Generation Resources, to match ERCOT’s forecasted Load, subject to all transmission constraints and Resource performance characteristics.  The RUC process takes into account Resources already committed in the Current Operating Plans (COPs), Resources already committed in previous RUCs, and Resource capacity already committed to provide Ancillary Service.  The formulation of the RUC objective function must employ penalty factors on violations of security constraints. The objective of the RUC process is to minimize costs based on Three-Part Supply Offers, substituting a proxy Energy Offer Curve for the Energy Offer Curve, over the RUC Study Period.

(2)	The RUC process can recommend Resource decommitment.  ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unresolvable. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment.  In addition, the HRUC process provides decision support to ERCOT regarding a Resource decommitment requested by a Qualified Scheduling Entity (QSE).

(3)	ERCOT shall review the RUC-recommended Resource commitments to assess feasibility and shall make any changes that it considers necessary, in its sole discretion.  ERCOT may deselect Resources recommended in DRUC and in all HRUC processes if in ERCOT’s sole discretion there is enough time to commit those Resources in the future HRUC processes, taking into account the Resources’ start-up times, to meet ERCOT System reliability.  Prior to receiving the RUC Instruction, QSEs may self-commit the Generation Resource.  ERCOT shall issue RUC Instructions to each QSE specifying its Resources that have been committed as a result of the RUC process.  ERCOT shall, within one day after making any changes to the RUC-recommended commitments, post to the MIS Secure Area any changes that ERCOT made to the RUC-recommended commitments with an explanation of the changes.

[NPRR207: Replace paragraph (3) above with the following upon system implementation:] (3) ERCOT shall review the RUC-recommended Resource commitments to assess feasibility and shall make any changes that it considers necessary, in its sole discretion. ERCOT may deselect Resources recommended in DRUC and in all HRUC processes if in ERCOT’s sole discretion there is enough time to commit those Resources in the future HRUC processes, taking into account the Resources’ start-up times, to meet ERCOT System reliability and shall issue a RUC Notification to the deselected Resources. Prior to receiving the RUC Instruction, QSEs may self-commit the Generation Resource. ERCOT shall issue RUC Instructions to each QSE specifying its Resources that have been committed as a result of the RUC process. ERCOT shall, within one day after making any changes to the RUC-recommended commitments, post to the MIS Secure Area any changes that ERCOT made to the RUC-recommended commitments with an explanation of the changes.

(4)	To determine the projected energy output level of each Resource and to project potential congestion patterns for each hour of the RUC, ERCOT shall calculate proxy Energy Offer Curves based on the Mitigated Offer Caps for the type of Resource as specified in Section 4.4.9.4, Mitigated Offer Cap and Mitigated Offer Floor, for use in the RUC.  Proxy Energy Offer Curves are calculated by multiplying the Mitigated Offer Cap by a constant selected by ERCOT from time to time that is no more than 0.10% and applying the cost for all Generation Resource output between High Sustained Limit (HSL) and Low Sustained Limit (LSL).

(5)	ERCOT shall use the RUC process to evaluate the need to commit Resources for which a QSE has submitted Three-Part Supply Offers and other available Off-Line Resources in addition to Resources that are planned to be On-Line during the RUC Study Period.  All of the above commitment information must be as specified in the QSE’s COP.

(6)	ERCOT shall create Three-Part Supply Offers for all Resources that did not submit a Three-Part Supply Offer, but are specified as available but Off-Line, excluding Resources with a Resource Status of EMR, in a QSE’s COP.  For such Resources, ERCOT shall use in the RUC process 150% of any approved verifiable Startup Cost and verifiable minimum-energy cost or if verifiable costs have not been approved, the applicable Resource Category Generic Startup Offer Cost and the applicable Resource Category Generic Minimum-Energy Offer Cost as described specified in Section 4.4.9.2.3, Startup Offer and Minimum-Energy Offer Generic Caps, registered with ERCOT.  However for Settlement purposes, ERCOT shall use any approved verifiable Startup Costs and verifiable minimum-energy cost for such Resources, or if verifiable costs have not been approved, the applicable Resource Category Generic Startup Offer Cost and Generic Minimum-Energy Offer Cost.

(7)	The RUC process must treat all Resource capacity providing Ancillary Service as unavailable for the RUC Study Period, unless that treatment leads to infeasibility (i.e., that capacity is needed to resolve some local transmission problem that cannot be resolved by any other means).  In such cases, ERCOT shall inform each affected QSE of the amount of its Resource capacity that does not qualify to provide Ancillary Service, and the projected hours for which this is the case.  In that event, the affected QSE may, under Section 6.4.8.1.2, Replacement of Undeliverable Ancillary Service Due to Transmission Constraints, either:

(a) 	Substitute capacity from Resources represented by that QSE;

(b)	Substitute capacity from other QSEs using Ancillary Service Trades; or

(c)	Ask ERCOT to replace the capacity.

(8)	Factors included in the RUC process are:

(a)	ERCOT System-wide hourly Load forecast allocated appropriately over Load buses;

(b)	Transmission constraints – Transfer limits on energy flows through the electricity network;

(i)	Thermal constraints – protect transmission facilities against thermal overload;

(ii)	Generic constraints – protect the transmission system against transient instability, dynamic instability or voltage collapse;

(c)	Planned transmission topology;

(d)	Energy sufficiency constraints;

(e)	Inputs from the COP, as appropriate;

(f)	Inputs from Resource Parameters, as appropriate;

(g)	Each Generation Resource’s Minimum-Energy Offer and Startup Offer, from its Three-Part Supply Offer;

(h)	Any Generation Resource that is Off-Line and available but does not have a Three-Part Supply Offer;

(i)	Forced Outage information; and

(j)	Inputs from the eight-day look ahead planning tool, which may potentially keep a unit On-Line (or start a unit for the next day) so that a unit minimum duration between starts does not limit the availability of the unit (for security reasons).

(9)	The HRUC process and the DRUC process are as follows:

(a)	The HRUC process uses current Resource Status for the initial condition for the first hour of the RUC Study Period.  All HRUC processes use the projected status of transmission breakers and switches starting with current status and updated for each remaining hour in the study as indicated in the COP for Resources and in the Outage Scheduler for transmission elements.

(b)	The DRUC process uses the Day-Ahead forecast of total ERCOT Load for each hour of the Operating Day.  The HRUC process uses the current hourly forecast of total ERCOT Load for each hour in the RUC Study Period.

(c)	The DRUC process uses the Day-Ahead weather forecast for each hour of the Operating Day.  The HRUC process uses the weather forecast information for each hour of the balance of the RUC Study Period.

(10)	A QSE that has one or more of its Resources RUC-committed to provide Ancillary Services must increase its Ancillary Service Supply Responsibility by the total amount of RUC-committed Ancillary Service quantities.  The QSE may only use a RUC-committed Resource to meet its Ancillary Service Supply Responsibility during that Resource’s RUC-Committed Interval if the Resource has been committed by the RUC process to provide Ancillary Service.  The QSE shall indicate the exact amount and type of Ancillary Service for which it was committed as the Resource’s Ancillary Service Resource Responsibility and Ancillary Services Schedule for the RUC-Committed Intervals for both telemetry and COP information provided to ERCOT.  Upon deployment of the Ancillary Services, the QSE shall adjust its Ancillary Services Schedule to reflect the amounts requested in the deployment.

5.5.3	Communication of RUC Commitments and Decommitments

(1)	The output of the RUC process is the cleared Resource commitments and decommitments.

(2)	ERCOT shall notify each QSE in the Day-Ahead of the DRUC Resource commitments and advisory decommitments that have been cleared by the RUC for the Resources that QSE represents.  ERCOT shall notify each QSE of the HRUC Resource commitments and decommitments that have been cleared by the RUC for the Resources that QSE represents.  Resource commitments must include the start interval and duration for which the Resource is required to be at least at LSL.  Resource decommitments must include the interval in which the Resource is required to be Off-Line, duration, and reason for the decommitment.

(3)	If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment.

(4)	The QSE shall acknowledge the notice or commitment or decommittment by changing the Resource Status of the affected Resources in the COP for RUC-Committed Intervals.

(5)	At any time during the Adjustment Period, ERCOT shall notify the QSE representing an RMR Unit or a Synchronous Condenser Unit of any modification to the Delivery Plan for the RMR Unit or the Synchronous Condenser Unit made as a result of an HRUC process.

5.6	RUC Cost Eligibility

5.6.1	Verifiable Costs

(1)	The Qualified Scheduling Entity (QSE) is responsible for submitting verifiable costs unless both the QSE and Resource Entity agree that the Resource Entity will have this responsibility, in which case both the QSE and Resource Entity shall submit an affidavit to ERCOT stating this arrangement.  Notwithstanding the foregoing, QSEs that submit Power Purchase or Tolling Agreements (PPAs) do not have the option of allowing Resource Entities to file verifiable costs.

(2)	Make-Whole Payments for a Resource are based on the Startup Offers and Minimum-Energy Offers for the Resource, limited by caps.  Until ERCOT approves verifiable unit-specific costs for that Resource, the caps are the Resource Category Startup Generic Cap and the Resource Category Minimum-Energy Generic Cap.  When ERCOT approves verifiable unit-specific costs for that Resource the caps are those verifiable unit-specific costs.  A QSE or Resource Entity may file verifiable unit-specific costs for a Resource at any time, but it must file those costs no later than 30 days after five Reliability Unit Commitment (RUC) events for that Resource in a calendar year.  A RUC event begins when a Resource receives a RUC instruction to come or stay On-Line and ends the later of when the Resource shuts down or the end of the Operating Day.  The most recent ERCOT-approved verifiable costs must be used going forward.

(3)	These unit-specific verifiable costs may include and are limited to the following average incremental costs:

(a)	Allocation of maintenance requirements based on number of starts between maintenance events using, at the option of the QSE or Resource Entity, either:

(i)	Manufacturer-recommended maintenance schedule;

(ii)	Historical data for the unit and actual maintenance practices; or

(iii)	Another method approved in advance by ERCOT in writing;

(b)	Startup fuel calculations based on recorded actual measured flows when the data is available or based on averages of historical flows for similar starts (for example, hot, cold, intermediate) when actual data is not available.  Startup fuel will include filing separately the startup fuel required to reach breaker close and fuel after breaker close to Low Sustained Limit (LSL).  Any fuel required to shutdown a resource will be submitted as the fuel from breaker open to shutdown;

(c)	Operation costs;

(d)	Chemical costs;

(e)	Water costs;

(f)	Emission credits; and

(g)	Nodal Implementation Surcharges (NISs).

(4)	Standard Operations and Maintenance (O&M) costs pursuant to paragraph (6) below may be used in lieu of the incremental O&M costs set forth in items (3)(a), (c), (d) and (e) above.

(5)	These unit-specific verifiable costs may not include:

(a)	Fixed costs, which are any cost that is incurred regardless of whether the unit is deployed or not; and

(b)	Costs for which the QSE or Resource Entity cannot provide sufficient documentation for ERCOT to verify the costs.

(6)	At their election, QSEs or Resource Entities may receive standard O&M costs for both startup and minimum energy until January 1, 2012.  This election may be made by submitting an election form to ERCOT.  If a QSE or Resource has received final approval for actual verifiable O&M costs under the verifiable cost process, it may not elect to receive standard O&M costs.  Standard O&M costs are defined as follows:

| Resource Category Start Year = 2009 | Cold Startup ($/start) | Intermediate Startup ($/start) | Hot Startup ($/start) | Variable O&M ($/MWh) |
| --- | --- | --- | --- | --- |
| Aeroderivative simple cycle commissioned after 1996 | 1,000.00 | 1,000.00 | 1,000.00 | 3.94 |
| Reciprocating Engine | 487.00 | 487.00 | 487.00 | 5.09 |
| Simple cycle ≤ 90 MW | 2,300.00 | 2,300.00 | 2,300.00 | 3.94 |
| Simple cycle ≥ 90 MW | 5,000.00 | 5,000.00 | 5,000.00 | 3.94 |
| Combined cycle: for each Combined-Cycle Configuration, the Startup Cost for that configuration is the sum of the Startup Costs for each unit within that configuration as follows: |  |  |  | 3.19 |
| Combustion turbine < 90MW | 2,300.00 | 2,300.00 | 2,300.00 |  |
| Combustion turbine ≥ 90 MW | 5,000.00 | 5,000.00 | 5,000.00 |  |
| Steam turbine | 3,000.00 | 2,250.00 | 1,250.00 |  |
| Gas-steam non-reheat boiler | 2,310.00 | 1,732.50 | 866.25 | 7.08 |
| Gas-steam reheat boiler | 3,000.00 | 2,250.00 | 1,125.00 | 7.08 |
| Gas-steam supercritical boiler | 4,800.00 | 3,600.00 | 1,800.00 | 7.08 |
| Nuclear, coal, lignite and hydro | 7,200.00 | 5,400.00 | 2,700.00 | 5.02 |
| Renewable | Not Applicable | Not Applicable | Not Applicable | 5.50 |

(a)	If the QSE or Resource Entity chooses to utilize the standard O&M costs for O&M, standard O&M costs will be used by ERCOT going forward until either:

(i)	Verifiable variable O&M costs are filed; or

(ii)	ERCOT notifies the QSE or Resource Entity to update its verifiable costs as set forth in either paragraph (10) or (11) below.  If a Resource is receiving standard O&M costs, it may reelect standard O&M costs when resubmitting verifiable costs.

(7)	When submitting verifiable costs for combined cycle Resources, the QSE or Resource Entity must elect standard O&M costs for all Combined-Cycle Configurations or verifiable costs for all Combined-Cycle Configurations within the combined cycle train.

(8)	QSEs submitting PPAs as Resource-specific verifiable costs documentation are subject to the guidelines detailed below and in the Verifiable Cost Manual.

(a)	Only QSEs offering Three-Part Supply Offers for a specific Resource may submit a PPA as verifiable costs documentation.

(b)	A QSE submitting a PPA as verifiable costs documentation must represent 100% of the Resource’s capacity.

(c)	Only PPAs:

(i) 	Signed prior to July 16, 2008; and

(ii) 	Not between Affiliates, subsidiaries or partners will be accepted as verifiable cost documentation.

(d)	Verifiable costs for PPAs shall be capped at the level of the highest comparable Resource (referred to as the reference Resource) specific verifiable costs approved by ERCOT without a PPA.  The ERCOT approved verifiable costs for a PPA shall be equal to the lesser of:

(i) 	The cap as described in paragraph (d) above; and

(ii) 	The costs from the PPA.

(e)	ERCOT shall use the Resource actual fuel costs submitted by the QSE for startup and operation at minimum-energy level (LSL), and shall use the Resource Category Startup Offer Generic Costs as the cap for the O&M portion of the Startup Costs until ERCOT receives and approves comparable Resource specific verifiable costs.

(f)	PPAs will no longer be accepted as verifiable cost documentation after the primary term of the contract expires.

(g)	ERCOT shall produce a report each April that provides the percentage of RUC Make-Whole Payments for Resources with PPAs during the 12 months of the previous calendar year.  The report shall be based on the final Settlements and include the total number of Resources that used a PPA for their most recent verifiable cost submission that was approved by ERCOT.  ERCOT shall present the results of this study to the appropriate Technical Advisory Committee (TAC) subcommittee.

(h)	Notwithstanding anything to the contrary in this Section 5.6.1, QSEs representing PPAs may, at any time, submit data from a Resource as verifiable costs documentation and such documentation will be accepted for consideration by ERCOT.  A QSE submitting verifiable costs documentation pursuant to this paragraph shall not be required to submit a PPA to ERCOT for consideration for verifiable cost recovery.

(9)	The process for determining the verifiable actual costs must be developed by ERCOT, approved by the appropriate TAC subcommittee, and posted to the Market Information System (MIS) Secure Area within one Business Day after initial approval and after each approved change.

(10)	ERCOT shall notify a QSE to update verifiable cost data of a Resource when the Resource has received more than 50 RUC instructions meeting the criteria in Section 5.6.2, RUC Startup Cost Eligibility, in a year, but ERCOT may not request an update more frequently than annually.

(11)	ERCOT shall notify a QSE to update verifiable cost data of a Resource if at least five years have passed since ERCOT previously approved verifiable cost data for that Resource.

(12)	Within 30 days after receiving an update notice from ERCOT under any of paragraphs (10) or (11) above, a QSE or Resource Entity must submit verifiable cost data for the Resource.  Despite the provisions in paragraph (2) above, if the QSE or Resource Entity does not submit verifiable cost data within 30 days after receiving an update notice, then, until updated verifiable costs are approved, ERCOT shall determine payment using the lower of:

(a)	Resource Category Startup Generic and Resource Category Minimum-Energy Generic Caps; and

(b)	Current ERCOT-approved verifiable startup and minimum-energy costs.

(13)	Generation Entities that represent Reliability-Must Run (RMR) Resources shall submit to ERCOT, Startup and variable O&M Cost estimates to be used by ERCOT as proxies for verifiable Startup Cost and minimum-energy verifiable cost and for Settlement.  The ERCOT-approved verifiable Startup Cost estimate will equal the startup fuel estimate times the sum of the appropriate Fuel Index Price (FIP) or Fuel Oil Price (FOP) and the fuel adder, plus the startup O&M.  The ERCOT-approved minimum-energy verifiable cost estimate will equal the heat rate from the RMR Agreement contract times the sum of the appropriate FIP or FOP and the fuel adder, plus the variable O&M.  The O&M cost estimates shall be revised monthly to be consistent with the latest actual costs for the RMR Unit submitted in accordance with Section 3.14.1.12, Reporting Actual Eligible Cost.  The O&M values will be effective until updated costs have been submitted to ERCOT.

5.6.1.1	Verifiable Startup Costs

The unit-specific verifiable costs for starting a Resource for each cold, intermediate, and hot start condition, as determined using the data submitted under Section 5.6.1, Verifiable Costs, and the Resource Parameters for the Resource are:

(a) 	Actual fuel consumption rate per start (MMBtu/start) multiplied by a resource category generic fuel price (Fuel Index Price (FIP) * 1.X, Fuel Oil Price (FOP), or $1.50 per MMBtu, as applicable), where X = $0.50/fuel price.  A new X is effective the first and third Tuesday or each month.  The fuel price is equal to FIP from the Tuesday prior to the effective date;

(b) 	Unit-specific verifiable or standard O&M expenses; and

(c)	NIS to operate the Resource from breaker close to its LSL, as described in the Verifiable Cost Manual.

5.6.1.2	Verifiable Minimum-Energy Costs

(1)	The unit-specific verifiable minimum-energy costs for a Resource are:

(a) 	Actual fuel cost to operate the unit at its LSL; plus

(b) 	Verifiable or standard variable O&M expenses; plus

(c)	NIS to operate the unit at its LSL.

(2)	The QSE must submit the Resource’s cost information by season if the Resource’s costs vary by season.  For gas-fired units, the actual fuel costs must be calculated using the actual seasonal heat rate (which must be supplied to ERCOT with seasonal heat-rate test data) multiplied by the FIP * 1.X, where X = $0.50/fuel price.  A new X is effective the first and third Tuesday of each month.  The fuel price is equal to FIP from the Tuesday prior to the effective date.  For coal- and lignite-fired units, the actual fuel costs must be calculated using the actual seasonal heat rate multiplied by a deemed fuel price of $1.50 per MMBtu.  For fuel oil-fired operations, the number of gallons burned must be multiplied by the FOP.

5.6.2	RUC Startup Cost Eligibility

(1)	For purposes of this Section 5.6.2, all contiguous RUC-Committed Hours are considered as one RUC instruction.  For each Resource, only one Startup Cost is eligible per block of contiguous RUC-Committed Hours.

(2)	For a Resource’s Startup Costs in the Operating Day, per RUC instruction, to be included in the calculation of the RUC guarantee for that Operating Day, all the criteria below must be met:

(a) 	When the RUC instruction is given, the Resource must not be QSE-committed in the Settlement Interval immediately before the designated start hour or after the last hour of the RUC instruction;

(b)	A later RUC instruction or QSE commitment must not connect the designated start hour or last hour of the RUC instruction to a block of QSE-committed Intervals that was QSE-committed before the RUC instruction was given;

(c)	The generation breakers must have been open, as indicated by a telemetered Resource status of Off-Line, for at least five minutes during the six hours preceding the first RUC-Committed Hour; and

(d)	The generation breakers must have been closed, as indicated by a telemetered Resource status of On-Line, for at least one minute during the RUC commitment period or after the determined five-minute open breaker, as indicated by a telemetered Resource status of Off-Line, in the six hours preceding the first RUC-Committed Hour.

5.6.3	Forced Outage of a RUC-Committed Resource

(1)	The calculation of a Make-Whole Payment for a RUC-committed Resource that is eligible to receive startup costs under Section 5.6.2, RUC Startup Cost Eligibility, and that experiences a Forced Outage after unit synchronization is governed by Section 5.6.2.

(2)	If a RUC-committed Resource, which Resource is eligible to include startup costs in its RUC guarantee under Section 5.6.2 without considering the criteria in item (2)(d) of Section 5.6.2, that experiences startup failure that creates a Forced Outage before breaker close, ERCOT shall include the Resource’s submitted and approved verifiable actual costs in the Resource’s RUC guarantee, limited to the lesser of:

(a)	Costs that qualify as normal startup expenses, including fuel and operation and maintenance expenses, incurred before the event that caused the Forced Outage; or

(b)	Resource’s Startup Offer in the RUC.

(3)	The process for determining the verifiable actual costs for a startup attempt under item (2) above must be developed by ERCOT, approved by the appropriate TAC subcommittee, and posted to the MIS Secure Area within one Business Day after initial approval and after each approved change.

(4)	The verifiable actual costs for a startup attempt under item (2) above shall only be included in the Resource’s RUC guarantee upon QSE notification of the startup attempt under item (2) and approval of the verifiable actual costs under item (3) above.

5.6.4	Cancellation of a RUC Commitment

(1)	The calculation of payment for a RUC-committed Resource that is issued a RUC Cancellation instruction for the RUC commitment from ERCOT prior to breaker close shall be paid through the RUC Decommitment Payment as described in Section 5.7.3, Payment When ERCOT Decommits a QSE-Committed Resource.

(2)	A RUC-committed Resource that receives a RUC Cancellation instruction prior to breaker close may submit through the dispute process all incremental expenses associated with the RUC Cancellation of the RUC-committed Resource.  These costs include all costs that qualify as normal Startup Costs, O&M expenses and associated fuel expenses incurred for the attempted start.

(3)	The process for determining the verifiable actual costs for a RUC cancellation must be developed by ERCOT, approved by the appropriate TAC subcommittee, and posted to the MIS Secure Area within one Business Day after initial approval and after each approved change.

5.7	Settlement for RUC Process

5.7.1	RUC Make-Whole Payment

(1)	To make up the difference when the revenues that a Reliability Unit Commitment (RUC)-committed Resource receives are less than its costs as described in paragraph (2) below, ERCOT shall calculate a RUC Make-Whole Payment for that Operating Day for that Resource (whether committed by Day-Ahead RUC (DRUC) or Hourly RUC (HRUC)).

(2)	ERCOT shall pay to the Qualified Scheduling Entity (QSE) for the Resource a Make-Whole Payment if the RUC Guarantee calculated in Section 5.7.1.1, RUC Guarantee, is greater than the sum of:

(a)	RUC Minimum-Energy Revenue calculated in Section 5.7.1.2, RUC Minimum-Energy Revenue;

(b)	Revenue less cost above Low Sustained Limited (LSL) during RUC-Committed Hours calculated in Section 5.7.1.3, Revenue Less Cost Above LSL During RUC-Committed Hours; and

(c)	Revenue less cost during QSE Clawback Intervals calculated in Section 5.7.1.4, Revenue Less Cost During QSE Clawback Intervals.

(3)	The RUC Make-Whole Payment to the QSE for each RUC-committed Resource, including Reliability Must-Run (RMR) Units, for each RUC-Committed Hour in an Operating Day is calculated as follows:

RUCMWAMTq,r,h	=	(-1) * Max (0, RUCGq,r,d – RUCMEREVq,r,d – RUCEXRRq,r,d – RUCEXRQCq,r,d) / RUCHRq,r,d

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCMWAMTq,r,h | $ | RUC Make-Whole Payment—The RUC Make-Whole Payment to the QSE for Resource r, for each RUC-Committed Hour of the Operating Day. When one or more Combined Cycle Generation Resources are committed by RUC, payment is made to the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCGq,r,d | $ | RUC Guarantee—The sum of eligible Startup Costs and minimum-energy costs for Resource r during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.1. When one or more Combined Cycle Generation Resources are committed by RUC, guaranteed costs are calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCMEREVq,r,d | $ | RUC Minimum-Energy Revenue—The sum of the energy revenues for Resource r’s generation up to LSL during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.2. When one or more Combined Cycle Generation Resources are committed by RUC, minimum-energy revenue is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCEXRRq,r,d | $ | Revenue Less Cost Above LSL During RUC-Committed Hours—The sum of the total revenue for Resource r operating above its LSL less the cost during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.3. When one or more Combined Cycle Generation Resources are committed by RUC, revenue less cost above LSL is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCEXRQCq,r,d | $ | Revenue Less Cost During QSE Clawback Intervals—The sum of the total revenue for Resource r less the cost during all QSE Clawback Intervals, for the Operating Day. See Section 5.7.1.4. When one or more Combined Cycle Generation Resources are committed by RUC, revenue less cost during QSE Clawback Intervals is calculated for the Combined Cycle Train for all Combined Cycle Generation Resources earning revenue in QSE Clawback Intervals. |
| RUCHRq,r,d | None | RUC Hour—The total number of RUC-Committed Hours, for Resource r for the Operating Day. When one or more Combined Cycle Generation Resources are committed by RUC, the total number of RUC-Committed Hours is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| q | None | A QSE. |
| r | None | A RUC-committed Generation Resource. |
| d | None | An Operating Day containing the RUC-commitment. |
| h | None | An hour in the RUC-commitment period. |

5.7.1.1	RUC Guarantee

(1)	The allowable Startup Costs and minimum-energy costs of a Resource committed by RUC is the RUC Guarantee.  The RUC Guarantee minimum-energy costs are prorated according to the actual generation when the Resource’s average output during a 15-minute Settlement Interval is below the corresponding LSL.

(2)	The SUPR, MEPR and LSL used to calculate the RUC Guarantee for a Combined Cycle Train are the SUPR, MEPR and LSL that correspond to the Combined Cycle Generation Resource, within the Combined Cycle Train, that is RUC-committed for the hour.

(3)	The RUC Guarantee is calculated for non-Combined Cycle Trains as follows:

RUCGq,r,d	=	 Σs(SUPRq,r,s * RUCSUFLAGq,r,s) + Σi(MEPRq,r,i * Min ((LSLq,r,i * (¼)), RTMGq,r,i))

(4)	The RUC Guarantee is calculated for Combined Cycle Trains as follows:

RUCGq,r,d	=	(SUPRq,r,s * RUCSUFLAGq,r,s) +

Σt(MAX (0, SUPR - SUPR)) +

Σi(MEPRq r,i * Min ((LSLq,r,i * (¼)), RTMGq,r i))

(a)	If a Combined Cycle Train transitions to a RUC-committed configuration from a QSE-committed or other RUC-committed configuration, the transition is calculated as follows:

MAX (0, SUPRafterCCGR – SUPRbeforeCCGR)

(b)	If a Combined Cycle Train transitions to a QSE-committed configuration from a RUC-committed configuration, the transition is calculated as follows:

MAX (0, SUPRbeforeCCGR – SUPRafterCCGR)

(5)	If a validated Three-Part Supply Offer has been submitted for a Resource for the RUC, then the RUC Guarantee for that Resource is based on the Startup Offer and Minimum-Energy Offer in that validated Three-Part Supply Offer.  If a validated Three-Part Supply Offer has not been submitted for a Resource for the RUC and ERCOT has not yet approved verifiable unit-specific costs for the Resource, then the RUC Guarantee for a Resource is based on the Resource Category Startup Generic Cap and the Resource Category Minimum-Energy Generic Cap.  If a validated Three-Part Supply Offer has not been submitted for a Resource for the RUC and ERCOT has approved verifiable unit-specific costs for the Resource, then the RUC Guarantee for a Resource is based on the most recent ERCOT-approved verifiable unit-specific costs for that Resource.

(a)	If the QSE submitted a validated Three-Part Supply Offer,

Then, 		SUPRq,r,s	=	SUOq,r,s

MEPRq,r,i	=	MEOq,r,i

Otherwise, 	SUPRq,r,s 	= 	SUCAPq,r,s

MEPRq,r,i 	= 	MECAPq,r,i

(b)	If ERCOT has approved verifiable Startup Costs and minimum-energy costs for the Resource,

Then, 		SUCAP q, r, s	=	verifiable Startup Costs q, r, s

MECAPq,r,i	=	verifiable minimum-energy costs q, r, i

Otherwise, 	SUCAP q, r, s 	= 	RCGSC s

MECAP q, r, i	= 	RCGMEC i

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCGq,r,d | $ | RUC Guarantee—The sum of eligible Startup Costs and minimum-energy costs for Resource r during all RUC-Committed Hours, for the Operating Day. When one or more Combined Cycle Generation Resources are committed by RUC, guaranteed costs are calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| SUPRq,r,s | $/Start | Startup Price per start—The settlement price for Resource r for the start s. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| SUOq,r,s | $/Start | Startup Offer per start—Represents an offer for all costs incurred by Generation Resource r in starting up and reaching the Resource’s LSL, minus the average energy produced during the time period between breaker close and LSL multiplied by the heat rate proxy multiplied by the appropriate Fuel Index Price (FIP) or Fuel Oil Price (FOP), as described in the Verifiable Cost Manual. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| SUCAPq,r,s | $/Start | Startup Cap—The amount used for Resource r as Startup Costs if the QSE did not submit a validated Three-Part Supply Offer. The cap is the RCGSC unless ERCOT has approved verifiable unit-specific Startup Costs for that Resource, in which case the startup cap is the verifiable unit-specific Startup Cost. See Section 5.6.1, Verifiable Costs, for more information on verifiable costs. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RCGSCs | $/Start | Resource Category Generic Startup Cost—The Resource Category Generic Startup Cost cap for the category of the Resource, according to Section 4.4.9.2.3, Startup Offer and Minimum-Energy Offer Generic Caps, for the Operating Day. |
| RUCSUFLAGq,r,s | none | RUC Startup Flag—The flag that indicates whether or not the start s for Resource r is eligible for RUC Make-Whole Payment. Its value is one if eligible; otherwise, zero. See Section 5.6.2, RUC Startup Cost Eligibility, and Section 5.6.3, Forced Outage of RUC-Committed Resource, for more information on startup eligibility. For a Combined Cycle Train, the Resource r must be one of the registered Combined Cycle Generation Resources within the Combined Cycle Train. When one or more Combined Cycle Generation Resources are committed by RUC, the RUC Startup Flag is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| MEPRq,r,i | $/MWh | Minimum-Energy Price—The settlement price for Resource r for minimum energy for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MEOq,r,i | $/MWh | Minimum-Energy Offer—Represents an offer for the costs incurred by Resource r in producing energy at the Resource’s LSL for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MECAPq,r,i | $/MWh | Minimum-Energy Cap—The amount used for Resource r for minimum-energy costs if the QSE did not submit a validated Three-Part Supply Offer. The cap is the RCGMEC unless ERCOT has approved verifiable unit-specific minimum energy costs for that Resource, in which case the Minimum-Energy Cap is the verifiable unit-specific minimum energy cost. See Section 5.6.1 for more information on verifiable costs. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RCGMECi | $/MWh | Resource Category Generic Minimum-Energy Cost—The Resource Category Generic Minimum Energy Cost cap for the category of the Resource, according to Section 4.4.9.2.3, for the Operating Day. |
| RTMGq,r,i | MWh | Real-Time Metered Generation—The Resource r’s metered generation for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train. |
| LSLq,r,i | MW | Low Sustained Limit—The LSL of Generation Resource r represented by QSE q for the hour that includes the Settlement Interval i, as submitted in the Current Operating Plan (COP). Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| q | none | A QSE. |
| r | none | A RUC-committed Generation Resource. |
| d | none | An Operating Day containing the RUC-commitment. |
| i | none | A 15-minute Settlement Interval within the hour that includes a RUC-commitment. |
| s | none | A start that is eligible to have its costs included in the RUC Guarantee. |
| t | none | A transition that is eligible to have its costs included in the RUC Guarantee. |
| afterCCGR | none | The Combined Cycle Generation Resource to which a Combined Cycle Train transitions. |
| beforeCCGR | none | The Combined Cycle Generation Resource from which a Combined Cycle Train transitions. |

5.7.1.2	RUC Minimum-Energy Revenue

(1)	The energy revenue for a Resource’s generation up to LSL during all RUC-Committed Hours of the Operating Day is RUC Minimum-Energy Revenue.

(2)	The LSL used to calculate RUC Minimum-Energy Revenue for a Combined Cycle Train is the LSL that corresponds to the Combined Cycle Generation Resource, within the Combined Cycle Train, that is RUC-committed for the hour.

(3)	For each RUC-committed Resource, RUC Minimum-Energy Revenue is calculated as follows:

RUCMEREVq,r,d	=	Σi(RTSPPp,i * Min (RTMGq,r,i, (LSLq,r,i * (¼))))

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCMEREVq,r,d | $ | RUC Minimum-Energy Revenue—The sum of the energy revenues for Resource r’s generation up to LSL during all RUC-Committed Hours, for the Operating Day. When one or more Combined Cycle Generation Resources are committed by RUC, RUC Minimum-Energy Revenue is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RTSPPp,i | $/MWh | Real-Time Settlement Point Price—The Real-Time Settlement Point Price at the Resource Node for the Settlement Interval i. |
| RTMGq,r,i | MWh | Real-Time Metered Generation—The Resource r’s metered generation for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train. |
| LSLq,r,i | MW | Low Sustained Limit—The LSL of Generation Resource r represented by QSE q for the hour that includes the Settlement Interval i, as submitted in the COP. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| q | none | A QSE. |
| r | none | A RUC-committed Generation Resource. |
| d | none | An Operating Day containing the RUC-commitment. |
| p | none | A Resource Node Settlement Point. |
| i | none | A 15-minute Settlement Interval within the hour that includes a RUC-commitment. |

5.7.1.3	Revenue Less Cost Above LSL During RUC-Committed Hours

(1)	The total revenue for a Resource operating above its LSL less the cost based on the Resource’s Energy Offer Curve capped by the Energy Offer Curve Cap (as described in Sections 4.4.9.3, Energy Offer Curve, and 4.4.9.3.3, Energy Offer Curve Caps for Make-Whole Calculation Purposes) or proxy Energy Offer Curve described in Section 6.5.7.3, Security Constrained Economic Dispatch, as applicable, during all RUC-Committed Hours of the Operating Day is Revenue Less Cost Above LSL During RUC-Committed Hours.

(2)	The LSL and RTAIEC used to calculate Revenue Less Cost Above LSL During RUC-Committed Hours for a Combined Cycle Train are the LSL and RTAIEC that correspond to the Combined Cycle Generation Resource, within the Combined Cycle Train, that is RUC-committed for the hour.

(3)	For each RUC-committed Resource, Revenue Less Cost Above LSL During RUC-Committed Hours is calculated as follows:

RUCEXRRq,r,d   =   Max {0, Σi[RTSPPp,i * Max (0, RTMGq,r,i – (LSLq,r,i * (¼)))

+ (-1) * (VSSVARAMTq,r,i + VSSEAMTq,r,i)

+ (-1) * EMREAMTq,r,i

– RTAIECq,r,i * Max (0, RTMGq,r,i – (LSLq,r,i * (¼)))]}

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCEXRRq,r,d | $ | Revenue Less Cost Above LSL During RUC-Committed Hours—The sum of the total revenue for Resource r operating above its LSL less the cost during all RUC-Committed Hours, for the Operating Day. When one or more Combined Cycle Generation Resources are committed by RUC, revenue less cost above LSL is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RTSPPp,i | $/MWh | Real-Time Settlement Point Price—The Real-Time Settlement Point Price at the Resource’s Settlement Point for the Settlement Interval i. |
| RTAIECq,r,i | $/MWh | Real-Time Average Incremental Energy CostThe average incremental energy cost for Resource r, calculated using the Energy Offer Curve capped by the Energy Offer Curve Cap, for the Resource’s generation above the LSL for the Settlement Interval i. See Section 4.6.5, Calculation of “Average Incremental Energy Cost” (AIEC). Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RTMGq,r,i | MWh | Real-Time Metered Generation—The Resource r’s metered generation for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train. |
| LSLq,r,i | MW | Low Sustained Limit—The LSL of Generation Resource r represented by QSE q for the hour that includes the Settlement Interval i, as submitted in the COP. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| VSSVARAMTq,r,i | $ | Voltage Support Service VAr Amount by interval—The payment to the QSE for the Voltage Support Service (VSS) provided by Generation Resource r for the 15-minute Settlement Interval i. See Section 6.6.7.1, Voltage Support Service Payments. Payment for VSS is made to the Combined Cycle Train. |
| VSSEAMTq,r,i | $ | Voltage Support Service Energy Amount by interval—The lost opportunity payment to the QSE for ERCOT-directed VSS from the Generation Resource r for the 15-minute Settlement Interval i. See Section 6.6.7.1. Payment for emergency energy is made to the Combined Cycle Train. |
| EMREAMTq,r,i | $ | Emergency Energy Amount by interval—The payment to the QSE as additional compensation for the additional energy produced by the Generation Resource r in Real-Time during the Emergency Condition, for the 15-minute Settlement Interval i. See Section 6.6.9.1, Payment for Emergency Power Increase Directed by ERCOT. Payment for emergency energy is made to the Combined Cycle Train. |
| q | none | A QSE. |
| r | none | A RUC-committed Generation Resource. |
| d | none | An Operating Day containing the RUC-commitment. |
| p | none | A Resource Node Settlement Point. |
| i | none | A 15-minute Settlement Interval within the hour that includes a RUC instruction. |

5.7.1.4	Revenue Less Cost During QSE Clawback Intervals

(1)	The total revenue for a Resource less the cost based on the Resource’s Energy Offer Curve capped by the Energy Offer Curve Cap (as described in Sections 4.4.9.3, Energy Offer Curve, and 4.4.9.3.3, Energy Offer Curve Caps for Make-Whole Calculation Purposes) or proxy Energy Offer Curve described in Section 6.5.7.3, Security Constrained Economic Dispatch, as applicable, during all QSE Clawback Intervals of the Operating Day is Revenue Less Cost During QSE-Clawback Intervals.

(2)	The MEPR, LSL and RTAIEC used to calculate Revenue Less Cost During QSE Clawback Intervals for a Combined Cycle Train is the MEPR, LSL and RTAIEC that corresponds to the Combined Cycle Generation Resource, within a Combined Cycle Train, that operates in Real-Time for the QSE Clawback Interval.

(3)	For each QSE Clawback Interval, Revenue Less Cost During QSE Clawback Intervals is calculated as follows:

RUCEXRQCq,r,d		=	Max {0, Σi[(RTSPPp,i * RTMGq,r,i)
+ (-1) * (VSSVARAMTq,r,i + VSSEAMTq,r,i)

+ (-1) * EMREAMTq,r,i

– [MEPRq,r,i * Min (RTMGq,r,i, (LSLq,r,i * (¼)))]

– [RTAIECq,r,i * Max (0, RTMGq,r,i – (LSLq,r,i * (¼)))]]}

If the QSE submitted a validated Three-Part Supply Offer for the Resource,

Then, 		MEPRq,r,i	=	MEOq,r,i

Otherwise, 	MEPRq,r,i 	= 	MECAPq,r,i

If ERCOT has approved verifiable minimum-energy costs for the Resource,

Then,		MECAPq,r,i	=	verifiable minimum-energy costsq,r,i

Otherwise, 	MECAPq,r,i	= 	RCGMECi

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCEXRQCq,r,d | $ | Revenue Less Cost During QSE-Clawback Intervals—The sum of the total revenue for Resource r less the cost during all QSE-Clawback Intervals for the Operating Day. When one or more Combined Cycle Generation Resources are committed by RUC, Revenue Less Cost During QSE-Clawback Intervals is calculated for the Combined Cycle Train for all Combined Cycle Generation Resources earning revenue in QSE-Clawback Intervals. |
| RTSPPp,i | $/MWh | Real-Time Settlement Point Price—The Real-Time Settlement Point Price at the Resource’s Settlement Point for the Settlement Interval i. |
| MEPRq,r,i | $/MWh | Minimum-Energy Price—The Settlement price for Resource r for minimum energy for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MEOq,r,i | $/MWh | Minimum-Energy Offer—Represents an offer for the costs incurred by Resource r in producing energy at the Resource’s LSL for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MECAPq,r,i | $/MWh | Minimum-Energy Cap—The amount used for Resource r for minimum-energy costs if the QSE did not submit a validated Three-Part Supply Offer. The cap is the RCGMEC unless ERCOT has approved verifiable unit-specific minimum energy costs for that Resource, in which case the Minimum-Energy Cap is the verifiable unit-specific minimum energy cost. See Section 5.6.1, Verifiable Costs, for more information on verifiable costs. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RCGMECi | $/MWh | Resource Category Generic Minimum-Energy Cost—The Resource Category Generic Minimum-Energy Cost cap for the category of the Resource, according to Section 4.4.9.2.3, Startup Offer and Minimum-Energy Offer Generic Caps, for the Operating Day. |
| RTAIECq,r,i | $/MWh | Real-Time Average Incremental Energy CostThe average incremental energy cost for Resource r, calculated using the Energy Offer Curve capped by the Energy Offer Curve Cap, for the Resource’s generation above the LSL for the Settlement Interval i. See Section 4.6.5, Calculation of “Average Incremental Energy Cost” (AIEC). Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RTMGq,r,i | MWh | Real-Time Metered Generation—The Resource r’s metered generation for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train. |
| LSLq,r,i | MW | Low Sustained Limit—The LSL of Generation Resource r represented by QSE q for the hour that includes the Settlement Interval i, as submitted in the COP. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| VSSVARAMTq,r,i | $ | Voltage Support Service VAr Amount by interval—The payment to the QSE for the VSS provided by Generation Resource r for the 15-minute Settlement Interval i. See Section 6.6.7.1, Voltage Support Service Payments. Payment for VSS is made to the Combined Cycle Train. |
| VSSEAMTq,r,i | $ | Voltage Support Service Energy Amount by interval—The lost opportunity payment to the QSE for ERCOT-directed VSS from the Generation Resource r for the 15-minute Settlement Interval i. See Section 6.6.7.1. Payment for VSS is made to the Combined Cycle Train. |
| EMREAMTq,r,i | $ | Emergency Energy Amount by interval—The payment to the QSE as additional compensation for the additional energy produced by the Generation Resource r in Real-Time during the Emergency Condition, for the 15-minute Settlement Interval i. See Section 6.6.9.1, Payment for Emergency Power Increase Directed by ERCOT. Payment for emergency energy is made to the Combined Cycle Train. |
| q | none | A QSE. |
| r | none | A RUC-committed Generation Resource. |
| d | none | An Operating Day containing the RUC-commitment. |
| p | none | A Resource Node Settlement Point. |
| i | none | A 15-minute Settlement Interval within the hour that is identified as a QSE-Clawback Interval. |

5.7.2	RUC Clawback Charge

(1)	A QSE for a Resource shall pay a RUC Clawback Charge for the Operating Day if the RUC Guarantee is less than the sum of:

(a)	RUC Minimum-Energy Revenue calculated in Section 5.7.1.2, RUC Minimum-Energy Revenue;

(b)	Revenue Less Cost Above LSL During RUC-Committed Hours calculated in Section 5.7.1.3, Revenue Less Cost Above LSL During RUC-Committed Hours; and

(c)	Revenue Less Cost During QSE-Clawback Intervals calculated in Section 5.7.1.4, Revenue Less Cost During QSE Clawback Intervals.

(2)	The amount of the RUC Clawback Charge is a percentage of the difference calculated in paragraph (1) above.  Whether or not the QSE submits a Three-Part Supply Offer for a Resource in the Day-Ahead Market (DAM) determines the clawback percentage.  If the QSE submitted a validated Three-Part Supply Offer for the Resource into the DAM, then the clawback percentage in RUC-Committed Hours is 50% and the clawback percentage in QSE Clawback Intervals is 0%.  If not, then the clawback percentage in RUC-Committed Hours is 100% and the clawback percentage in QSE Clawback Intervals is 50%.

(3)	If an Energy Emergency Alert (EEA) is in effect for any hour that a Resource is RUC-committed, then in all RUC-Committed Hours of the Operating Day the clawback percentage is 0% if the QSE submitted a validated Three-Part Supply Offer for the Resource into the DAM and 50% otherwise.

(4)	For Combined Cycle Trains, if at least one Combined Cycle Generation Resource is offered into the DAM, then the Combined Cycle Train is considered to be offered into the DAM.

(5)	The RUC Clawback Charge for a Resource, including RMR Units, for each Operating Day is allocated evenly over the RUC-Committed Hours for that Resource.

(6)	For each RUC-committed Resource, the RUC Clawback Charge for each RUC-Committed Hour of the Operating Day is calculated as follows:

If (RUCMEREVq,r,d + RUCEXRRq,r,d – RUCGq,r,d) > 0,

Then,

RUCCBAMTq,r,h	=	[(RUCMEREVq,r,d + RUCEXRRq,r,d – RUCGq,r,d) * RUCCBFRq,r,d + RUCEXRQCq,r,d * RUCCBFCq,r,d] / RUCHRq,r,d

Otherwise,

RUCCBAMTq,r,h 	= [Max (0, RUCMEREVq,r,d + RUCEXRRq,r,d + RUCEXRQCq,r,d – RUCGq,r,d) * RUCCBFCq,r,d] / RUCHRq,r,d

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCCBAMTq,r,h | $ | RUC Clawback Charge––The RUC Clawback Charge to a QSE for Resource r as described in this Section, for each RUC-Committed Hour of the Operating Day for that Resource. When one or more Combined Cycle Generation Resources are committed by RUC, a charge is made to the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCGq,r,d | $ | RUC Guarantee—The sum of eligible Startup Costs and Minimum-Energy Costs for Resource r during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.1, RUC Guarantee. When one or more Combined Cycle Generation Resources are committed by RUC, guaranteed costs are calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCMEREVq,r,d | $ | RUC Minimum-Energy Revenue—The sum of the energy revenues for Resource r’s generation up to LSL during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.2. When one or more Combined Cycle Generation Resources are committed by RUC, RUC Minimum-Energy Revenue is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCEXRRq,r,d | $ | Revenue Less Cost Above LSL During RUC-Committed Hours—The sum of the total revenue for Resource r above the LSL less the cost during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.3. When one or more Combined Cycle Generation Resources are committed by RUC, Revenue Less Cost Above LSL During RUC-Committed Hours is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCEXRQCq,r,d | $ | Revenue Less Cost from QSE-Clawback Intervals—The sum of the total revenue for Resource r less the cost during all QSE-Clawback Intervals for the Operating Day. See Section 5.7.1.4. When one or more Combined Cycle Generation Resources are committed by RUC, Revenue Less Cost from QSE-Clawback Intervals is calculated for the Combined Cycle Train for all Combined Cycle Generation Resources earning revenue in QSE Clawback Intervals. |
| RUCCBFRq,r,d | none | RUC Clawback Factor for RUC-Committed Hours—The Resource r’s Clawback Factor for RUC-Committed Hours, which is 50% if a Three-Part Supply Offer was submitted and 100% otherwise. During EEA conditions, the Resource’s RUC Clawback Factor for RUC-Committed Hours is 0% if a Three-Part Supply Offer was submitted and 50% otherwise. When one or more Combined Cycle Generation Resources are committed by RUC, the RUC Clawback Factor for RUC-Committed Hours is determined for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCCBFCq,r,d | none | RUC Clawback Factor for QSE Clawback Intervals—The Resource r’s Clawback Factor for QSE Clawback Intervals, which is 0% if a Three-Part Supply Offer was submitted and 50% otherwise. When one or more Combined Cycle Generation Resources are committed by RUC, the RUC Clawback Factor for QSE Clawback Intervals is determined for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCHRq,r,d | none | RUC Hour—The total number of RUC-Committed Hours, for Resource r for the Operating Day. When one or more Combined Cycle Generation Resources are committed by RUC, the total number of RUC-Committed Hours is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| q | none | A QSE. |
| r | none | A RUC-committed Generation Resource. |
| d | none | An Operating Day containing the RUC-commitment. |
| h | none | An hour in the RUC-commitment period. |

[NPRR222: Replace the above Section 5.7.2, RUC Clawback Charge, with the following upon system implementation] 5.7.2 RUC Clawback Charge (1) A QSE for a Resource shall pay a RUC Clawback Charge for the Operating Day if the RUC Guarantee is less than the sum of: (a) RUC Minimum-Energy Revenue calculated in Section 5.7.1.2, RUC Minimum-Energy Revenue; (b) Revenue Less Cost Above LSL During RUC-Committed Hours calculated in Section 5.7.1.3, Revenue Less Cost Above LSL During RUC-Committed Hours; and (c) Revenue Less Cost During QSE-Clawback Intervals calculated in Section 5.7.1.4, Revenue Less Cost During QSE Clawback Intervals. (2) The amount of the RUC Clawback Charge is a percentage of the difference calculated in paragraph (1), above. Whether or not the QSE submits a Three-Part Supply Offer for a Resource in the Day-Ahead Market (DAM) determines the clawback percentage. If the QSE submitted a validated Three-Part Supply Offer for the Resource into the DAM, then the clawback percentage in RUC-Committed Hours is 50% for Resources that are not Half-Hour Start Units, the clawback percentage in RUC-Committed Hours is 0% for Resources that are Half-Hour Start Units and the clawback percentage in QSE Clawback Intervals is 0%. If the QSE did not submit a validated Three-Part Supply Offer for the Resource that is not a Half-Hour Start Unit, then the clawback percentage in RUC-Committed Hours is 100% and the clawback percentage in QSE Clawback Intervals is 50%. If the QSE did not submit a validated Three-Part Supply Offer for the Resource that is a Half-Hour Start Unit, then the clawback percentage for RUC-Committed Hours is 50% and the clawback percentage in QSE Clawback Intervals is 0%. (3) If an Energy Emergency Alert (EEA) is in effect for any hour that a Resource that is not a Half-Hour Start Unit is RUC-committed, then in all RUC-Committed Hours of the Operating Day the clawback percentage is 0% if the QSE submitted a validated Three-Part Supply Offer for the Resource into the DAM and 50% otherwise. If an EEA is in effect for any hour that a Resource that is a Half-Hour Start Unit is RUC-Committed, then in all RUC-Committed Hours of the Operating Day the clawback percentage is 0%. (4) For Combined Cycle Trains, if at least one Combined Cycle Generation Resource is offered into the DAM, then the Combined Cycle Train is considered to be offered into the DAM. (5) The RUC Clawback Charge for a Resource, including RMR Units, for each Operating Day is allocated evenly over the RUC-Committed Hours for that Resource. (6) For each RUC-committed Resource, the RUC Clawback Charge for each RUC-Committed Hour of the Operating Day is calculated as follows: If (RUCMEREVq,r,d + RUCEXRRq,r,d – RUCGq,r,d) > 0, Then, RUCCBAMTq,r,h = [(RUCMEREVq,r,d + RUCEXRRq,r,d – RUCGq,r,d) * RUCCBFRq,r,d + RUCEXRQCq,r,d * RUCCBFCq,r,d] / RUCHRq,r,d Otherwise, RUCCBAMTq,r,h = [Max (0, RUCMEREVq,r,d + RUCEXRRq,r,d + RUCEXRQCq,r,d – RUCGq,r,d) * RUCCBFCq,r,d] / RUCHRq,r,d The above variables are defined as follows: Variable; Unit; Definition. RUCCBAMTq,r,h; $; RUC Clawback Charge––The RUC Clawback Charge to a QSE for Resource r as described in this Section, for each RUC-Committed Hour of the Operating Day for that Resource. When one or more Combined Cycle Generation Resources are committed by RUC, a charge is made to the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources.. RUCGq,r,d; $; RUC Guarantee—The sum of eligible Startup Costs and Minimum-Energy Costs for Resource r during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.1, RUC Guarantee. When one or more Combined Cycle Generation Resources are committed by RUC, guaranteed costs are calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources.. RUCMEREVq,r,d; $; RUC Minimum-Energy Revenue—The sum of the energy revenues for Resource r’s generation up to LSL during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.2. When one or more Combined Cycle Generation Resources are committed by RUC, RUC Minimum-Energy Revenue is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources.. RUCEXRRq,r,d; $; Revenue Less Cost Above LSL During RUC-Committed Hours—The sum of the total revenue for Resource r above the LSL less the cost during all RUC-Committed Hours, for the Operating Day. See Section 5.7.1.3. When one or more Combined Cycle Generation Resources are committed by RUC, Revenue Less Cost Above LSL During RUC-Committed Hours is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources.. RUCEXRQCq,r,d; $; Revenue Less Cost from QSE-Clawback Intervals—The sum of the total revenue for Resource r less the cost during all QSE-Clawback Intervals for the Operating Day.. See Section 5.7.1.4. When one or more Combined Cycle Generation Resources are committed by RUC, Revenue Less Cost from QSE-Clawback Intervals is calculated for the Combined Cycle Train for all Combined Cycle Generation Resources earning revenue in QSE Clawback Intervals.. RUCCBFRq,r,d; none; RUC Clawback Factor for RUC-Committed Hours—The Resource r’s Clawback Factor is defined in paragraphs (2) and (3) above. When one or more Combined Cycle Generation Resources are committed by RUC, the RUC Clawback Factor for RUC-Committed Hours is determined for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources.. RUCCBFCq,r,d; none; RUC Clawback Factor for QSE Clawback intervals—The Resource r’s Clawback Factor is defined in paragraphs (2) and (3) above. When one or more Combined Cycle Generation Resources are committed by RUC, the RUC Clawback Factor for QSE Clawback Intervals is determined for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources.. RUCHRq,r,d; none; RUC Hour—The total number of RUC-Committed Hours, for Resource r for the Operating Day. When one or more Combined Cycle Generation Resources are committed by RUC, the total number of RUC-Committed Hours is calculated for the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources.. q; none; A QSE.. r; none; A RUC-committed Generation Resource.. d; none; An Operating Day containing the RUC-commitment.. h; none; An hour in the RUC-commitment period..

5.7.3	Payment When ERCOT Decommits a QSE-Committed Resource

(1)	If ERCOT decommits a QSE-committed Resource during the RUC process earlier than its scheduled shutdown within the Operating Day, then no compensation is due to the affected QSE from ERCOT.

(2)	If ERCOT decommits a QSE committed Resource that is not scheduled to shutdown within the Operating Day, then ERCOT shall pay the affected QSE an amount as calculated below for the hours of decommitment.  The number of continuous decommitted hours used in the calculation are the hours beginning with the first decommitted hour until the earlier of:

(a)	The hour ERCOT determines that the Resource may again be at LSL; and

(b)	The end of the last hour of the Operating Day.

(3)	If ERCOT decommits a QSE-committed Resource not scheduled to shutdown within the Operating Day, and the decommitment period spans more than one Operating Day, the RUC Decommitment Payment Amount shall be calculated and paid in the Operating Day in which the RUC decommitment originated.  The number of continuous decommitted hours used in the calculation are the hours beginning with the first decommitted hour until the end of the last hour of the Operating Day in which the RUC decommitment originated.

(4)	The payment for a RUC Cancellation instruction for a Resource is settled for each hour through an adjustment in the RUC Decommitment Payment Amount as shown in paragraph (7) below.

(5)	ERCOT shall produce a report each April that provides the percentage of the RUC Decommitment Payment Amounts that are a result of RUC cancellations during the 12 months of the previous calendar year.  The report shall be based on the Final Settlements.  ERCOT shall present the results of this study to the appropriate Technical Advisory Committee (TAC) subcommittee.

(6)	The SUPR, MEPR and LSL used to calculate payment when ERCOT decommits a QSE-committed Combined Cycle Train is the SUPR, MEPR and LSL that corresponds to the Combined Cycle Generation Resource, within the Combined Cycle Train, that is RUC-decommitted in the first hour of a contiguous decommitted period.

(7)	The payment for a RUC decommitment instruction for a Resource, including RMR Units, is calculated for each hour as follows:

RUCDCAMTq,r,h	=	(-1) * Max (0, (SUPRq,r,s - Σi(Max (0, MEPRq,r,i - RTSPPp,i) * (LSLq,r,i * (¼))))) / NCDCHRq,r,h

Where:

If the QSE submitted a validated Three-Part Supply Offer for the Resource,

Then, 		SUPRq,r,s	=	SUOq,r,s

MEPRq,r,i	=	MEOq,r,i

Otherwise, 	SUPRq,r,s 	= 	SUCAPq,r,s

MEPRq,r,i 	= 	MECAPq,r,i

If ERCOT has approved verifiable Startup Costs and minimum-energy costs for the Resource,

Then, 		SUCAPq,r,s	=	verifiable Startup Costsq,r,s

MECAPq,r,i	=	verifiable minimum-energy costsq,r,i

Otherwise, 	SUCAPq,r,s 	= 	RCGSCs

MECAPq,r,i	= 	RCGMECi

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCDCAMTq,r,h | $ | RUC Decommitment Payment Amount—The payment to the QSE for the Resource that was decommitted by ERCOT but that was not scheduled to shut down in the Operating Day, for each decommited hour of the Operating Day. When one or more Combined Cycle Generation Resources are decommitted by RUC, payment is made to the Combined Cycle Train for all RUC-decommitted Combined Cycle Generation Resources. |
| SUPRq,r,s | $/Start | Startup Price per start—The settlement price for Resource r for the start s. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| SUOq,r,s | $/Start | Startup Offer per start—Represents an offer for all costs incurred by Generation Resource r in starting up and reaching the Resource’s LSL, minus the average energy produced during the time period between breaker close and LSL multiplied by the heat rate proxy multiplied by the appropriate FIP or FOP, as described in the Verifiable Cost Manual. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| SUCAPq,r,s | $/Start | Startup Cap—The amount used for Resource r as Startup Costs if the QSE did not submit a validated Three-Part Supply Offer. The cap is the RCGSC unless ERCOT has approved verifiable unit-specific Startup Costs for that Resource, in which case the Startup Cap is the verifiable unit-specific Startup Cost. See Section 5.6.1, Verifiable Costs, for more information on verifiable costs. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RCGSCs | $/Start | Resource Category Generic Startup Cost—The Resource Category Startup Offer Generic Cap cost for the category of the Resource, according to Section 4.4.9.2.3, Startup Offer and Minimum-Energy Offer Generic Caps, for the Operating Day. |
| MEPRq,r,i | $/MWh | Minimum-Energy Price—The settlement price for Resource r for minimum energy for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MEOq,r,i | $/MWh | Minimum-Energy Offer—Represents an offer for the costs incurred by Resource r in producing energy at the Resource’s LSL for the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MECAPq,r,i | $/MWh | Minimum-Energy Cap—The amount used for Resource r for minimum-energy costs if the QSE did not submit a validated Three-Part Supply Offer. The cap is the RCGMEC unless ERCOT has approved verifiable unit-specific minimum energy costs for that Resource, in which case the Minimum-Energy Cap is the verifiable unit-specific minimum energy cost. See Section 5.6.1 for more information on verifiable costs. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RCGMECi | $/MWh | Resource Category Generic Minimum-Energy Cost—The Resource Category Minimum-Energy Generic Cap cost for the category of the Resource, according to Section 4.4.9.2.3. |
| LSLq,r,i | MW | Low Sustained Limit—The LSL of Generation Resource r represented by QSE q for the hour that includes the Settlement Interval i, as submitted in the COP. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RTSPPp,i | $/MWh | Real-Time Settlement Point Price—The Real-Time Settlement Point Price at the Resource’s Settlement Point for the Settlement Interval i. |
| NCDCHRq,r,h | none | Number of Continuous Decommitted Hours—The number of continuous decommitment hours for Resource r within an Operating Day. When one or more Combined Cycle Generation Resources are decommitted by RUC, the Number of Continuous Decommitted Hours is calculated for the Combined Cycle Train for all RUC-decommitted Combined Cycle Generation Resources. |
| q | none | A QSE. |
| r | none | A RUC-decommitted Generation Resource. |
| h | none | An hour in the RUC decommitment period. |
| p | none | A Resource Node Settlement Point. |
| s | none | A start. |
| i | none | A 15-minute Settlement Interval within the contiguous decommited period. |

5.7.4	RUC Make-Whole Charges

(1)	All QSEs that were capacity-short in each RUC will be charged for that shortage, as described in Section 5.7.4.1, RUC Capacity-Short Charge.  If the revenues from the charges under Section 5.7.4.1 are not enough to cover all RUC Make-Whole Payments for a Settlement Interval, then the difference will be uplifted to all QSEs on a Load Ratio Share (LRS) basis, as described in Section 5.7.4.2, RUC Make-Whole Uplift Charge.

(2)	To determine whether a QSE is capacity-short, the Short Term Wind Power Forecast (STWPF) for a Wind-powered Generation Resource (WGR) used in the corresponding RUC is considered the available capacity of the WGR when determining responsibility for the corresponding RUC charges, regardless of the Real-Time output of the WGR.

[NPRR210: Replace paragraph (2) above with the following upon system implementation:] (2) To determine whether a QSE is capacity-short, the Wind-powered Generation Resource Production Potential (WGRPP), as described in Section 4.2.2, Wind-powered Generation Resource Production Potential, for a Wind-powered Generation Resource (WGR) used in the corresponding RUC is considered the available capacity of the WGR when determining responsibility for the corresponding RUC charges, regardless of the Real-Time output of the WGR.

(3)	On a monthly basis, within ten days after the Initial Settlement of the last day of the month has been completed, ERCOT shall post on the Market Information System (MIS) Secure Area the total RUC Make-Whole Charges and RUC Clawback Payment Amounts, by Settlement Interval, by QSE capacity-shortfall and by amount uplifted.

5.7.4.1	RUC Capacity-Short Charge

The dollar amount charged to each QSE, due to capacity shortfalls for a particular RUC, for a 15-minute Settlement Interval, is the QSE’s shortfall ratio share multiplied by the total RUC Make-Whole Payments, including amounts for RMR Units, to all QSEs for that RUC, subject to a cap.  The cap on the charge to each QSE is two multiplied by the total RUC Make-Whole Payments, including amounts for RMR Units, for all QSEs multiplied by that QSE’s capacity shortfall for that RUC process divided by the total capacity of all RUC-committed Resources during that Settlement Interval for the RUC process.  That dollar amount charged to each QSE is calculated as follows:

RUCCSAMTruc,i,q	=	(-1) * Max [(RUCSFRSruc,i,q * RUCMWAMTRUCTOTruc,h), 
(2 * RUCSFruc,i,q * RUCMWAMTRUCTOTruc,h / RUCCAPTOTruc,h)] / 4

Where:

RUCMWAMTRUCTOTruc,h 	=	ΣqΣrRUCMWAMTruc,q,r,h

RUCCAPTOTruc,h	    	 =	ΣrHSLruc,h,r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCCSAMTruc,i,q | $ | RUC Capacity-Short Amount—The charge to a QSE, due to capacity shortfall for a particular RUC process, for the 15-minute Settlement Interval. |
| RUCMWAMTRUCTOTruc,h | $ | RUC Make-Whole Amount Total per RUC—The sum of RUC Make-Whole Payments for a particular RUC process, including amounts for RMR Units, for the hour that includes the 15-minute Settlement Interval. |
| RUCMWAMTruc,q,r,h | $ | RUC Make-Whole Payment—The RUC Make-Whole Payment to the QSE for Resource r, for a particular RUC process, for the hour that includes the 15-minute Settlement Interval. See Section 5.7.1, RUC Make-Whole Payment. When one or more Combined Cycle Generation Resources are committed by RUC, payment is made to the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| RUCSFRSruc,i,q | none | RUC Shortfall Ratio Share—The ratio of the QSE’s capacity shortfall to the sum of all QSEs’ capacity shortfalls for a particular RUC process, for the 15-minute Settlement Interval. See Section 5.7.4.1.1, Capacity Shortfall Ratio Share. |
| RUCSFruc,i,q | MW | RUC Shortfall—The QSE’s capacity shortfall for a particular RUC process for the 15-minute Settlement Interval. See formula in Section 5.7.4.1.1. |
| RUCCAPTOTruc,h | MW | RUC Capacity Total—The sum of the High Sustained Limits (HSLs) of all RUC-committed Resources for a particular RUC process, for the hour that includes the 15-minute Settlement Interval. See formula in Section 5.7.4.1.1. |
| HSLruc,h,r | MW | High Sustained Limit—The HSL of Generation Resource r as defined in Section 2, Definitions and Acronyms, for the hour that includes the Settlement Interval i. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| ruc | none | The RUC process for which the RUC Capacity-Short Charge is calculated. |
| i | none | A 15-minute Settlement Interval. |
| q | none | A QSE. |
| h | none | The hour that includes the Settlement Interval i. |
| r | none | A Generation Resource that is RUC-committed for the hour that includes the Settlement Interval i, as a result of a particular RUC process. |

5.7.4.1.1	Capacity Shortfall Ratio Share

(1)	In calculating the amount short for each QSE, the QSE must be given a capacity credit for its WGRs based on the HSL values entered into the COP by the QSE just prior to the RUC execution.  For WGRs, ERCOT shall use for Settlement purposes the COP and Trades Snapshot prior to the RUC regardless of Real-Time capacity or actual generation.  Therefore, the HASLSNAP and HASLADJ variables used below shall be equal to the HSL values entered into the QSE’s COP submitted prior to the RUC for WGRs.

(2)	In calculating the amount short for each QSE, the QSE must be given a capacity credit for non-wind Resources that were given notice of decommitment within the two hours before the Operating Hour as a result of the RUC process by setting the HASLSNAP and HASLADJ variables used below equal to the HASLSNAP value for the Resource immediately before the decommitment instruction was given.

(3)	In calculating the short amount for each QSE, if the High Ancillary Service Limit (HASL) for a Resource was credited to the QSE during the RUC snapshot but the Resource experiences a Forced Outage within two hours before the start of the Settlement Interval, then the HASL for that Resource is also credited to the QSE in the HASLADJ.

(4)	In calculating the short amount for each QSE, if the DCIMPSNAP was credited to the QSE during the RUC snapshot but the entire Direct Current Tie (DC Tie) experiences a Forced Outage within two hours before the start of the Settlement Interval, then the DCIMPSNAP is also credited to the QSE in the DCIMPADJ.

(5)	For Combined Cycle Generation Resources, if more than one Combined Cycle Generation Resource is shown On-Line in its COP for the same Settlement hour, then the provisions of paragraph (5)(a) of Section 3.9.1, Current Operating Plan (COP) Criteria, apply in the determination of the On-Line Combined Cycle Generation Resource for that Settlement hour.

(6)	The capacity shortfall ratio share of a specific QSE for a particular RUC process is calculated, for a 15-minute Settlement Interval, as follows:

RUCSFRSruc,i,q	=	RUCSFruc,i,q / RUCSFTOTruc,i

Where:

RUCSFTOTruc,i	=	ΣqRUCSFruc,i,q

(7)	The RUC Shortfall in MW for one QSE for one 15-minute Settlement Interval is:

RUCSFruc,i,q	=	Max (0, Max (RUCSFSNAP ruc,q,i, RUCSFADJ ruc,q,i) – Σz is prior to rucRUCCAPCREDIT q,i,z)

(8)	The RUC Shortfall in MW for one QSE for one 15-minute Settlement Interval, as measured at the snapshot, is:

RUCSFSNAP ruc,q,i	=	Max (0, ((ΣpRTAML q,p,i * 4) + Σp RTDCEXP q, p, i – RUCCAPSNAP ruc,q,i))

(9)	The amount of capacity that a QSE had according to the RUC snapshot for a 15-minute Settlement Interval is:

RUCCAPSNAP ruc,q,i =	ΣrHASLSNAPq,r,h + (RUCCPSNAPq,h – RUCCSSNAPq,h) + (ΣpDAEPq,p,h –ΣpDAESq,p,h) + (ΣpRTQQEPSNAPq,p,i – ΣpRTQQESSNAPq,p,i) +  Σp DCIMPSNAP q, p, i

(10)	The RUC Shortfall in MW for one QSE for one 15-minute Settlement Interval, as measured at Real-Time, but including capacity from WGRs as seen in the RUC snapshot, is:

RUCSFADJ ruc,q,i	=	Max (0, ((ΣpRTAMLq,p,i) *4) + Σp RTDCEXP q, p, i – (Σr=WGRsOnlyHASLSNAP ruc, q, r, h + RUCCAPADJq,i))

(11)	The amount of capacity that a QSE had in Real-Time for a 15-minute Settlement Interval, excluding capacity from WGRs, is:

RUCCAPADJq,i =	ΣrHASLADJq,r,h + (RUCCPADJq,h – RUCCSADJq,h) + (ΣpDAEPq,p,h – ΣpDAESq,p,h) + (ΣpRTQQEPADJq,p,i – ΣpRTQQESADJq,p,i) + Σp DCIMPADJ q, p, i

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCSFRSruc,i,q | none | RUC Shortfall Ratio Share—The ratio of the QSE’s capacity shortfall to the sum of all QSEs’ capacity shortfalls, for the RUC process, for the 15-minute Settlement Interval. |
| RUCSFruc,i,q | MW | RUC Shortfall—The QSE q’s capacity shortfall for the RUC process for the 15-minute Settlement Interval. |
| RUCSFTOTruc,i | MW | RUC Shortfall Total—The sum of all QSEs’ capacity shortfalls, for a RUC process, for a 15-minute Settlement Interval. |
| RUCSFSNAPruc,q,i | MW | RUC Shortfall at Snapshot—The QSE q’s capacity shortfall according to the snapshot for the RUC process for the 15-minute Settlement Interval. |
| RUCSFADJruc,q,i | MW | RUC Shortfall at Adjustment Period—The QSE q’s Adjustment Period capacity shortfall, including capacity from WGRs as seen in the snapshot for the RUC process, for the 15-minute Settlement Interval. |
| RUCCAPCREDITq,i,z | MW | RUC Capacity Credit by QSE—The capacity credit resulting from capacity paid through the RUC Capacity-Short Amount for the 15-minute Settlement Interval. |
| RTAMLq,p,i | MWh | Real-Time Adjusted Metered Load—The QSE q’s Adjusted Metered Load (AML) at the Settlement Point p for the 15-minute Settlement Interval. |
| RUCCAPSNAPruc,q,i | MW | RUC Capacity Snapshot at time of RUC—The amount of the QSE’s calculated capacity in the COP and Trades Snapshot for a 15-minute Settlement Interval. |
| HASLSNAPq,r,h | MW | High Ancillary Services Limit at Snapshot—The HASL of the Resource r represented by the QSE q, according to the COP and Trades Snapshot for the RUC process for the hour that includes the 15-minute Settlement Interval. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RTDCEXP q, p | MW | Real-Time DC Export per QSE per Settlement Point—The aggregated DC Tie Schedule through DC Tie p submitted by QSE q that is under the Oklaunion Exemption as an exporter from the ERCOT Region, for the 15-minute Settlement Interval. |
| DCIMPADJ q, p | MW | DC Import per QSE per Settlement Point—The approved aggregated DC Tie Schedule submitted by QSE q as an importer into the ERCOT System through DC Tie p according to the Adjustment Period snapshot, for the 15-minute Settlement Interval. |
| DCIMPSNAP q, p | MW | DC Import per QSE per Settlement Point—The approved aggregated DC Tie Schedule submitted by QSE q as an importer into the ERCOT System through DC Tie p, according to the snapshot for the RUC process for the hour that includes the 15-minute Settlement Interval. |
| RUCCPSNAPq,h | MW | RUC Capacity Purchase at Snapshot—The QSE q’s capacity purchase, according to the COP and Trades Snapshot for the RUC process for the hour that includes the 15-minute Settlement Interval. |
| RUCCSSNAPq,h | MW | RUC Capacity Sale at Snapshot—The QSE q’s capacity sale, according to the COP and Trades Snapshot for the RUC process for the hour that includes the 15-minute Settlement Interval. |
| RUCCAPADJq,i | MW | RUC Capacity Snapshot during Adjustment Period—The amount of the QSE’s calculated capacity in the RUC according to the COP and Trades Snapshot, excluding capacity for WGRs, at the end of the Adjustment Period for a 15-minute Settlement Interval |
| HASLADJq,r,h | MW | High Ancillary Services Limit at Adjustment Period—The HASL of a non-WGR r represented by the QSE q, according to the Adjustment Period snapshot, for the hour that includes the 15-minute Settlement Interval. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| RUCCPADJq,h | MW | RUC Capacity Purchase at Adjustment Period—The QSE q’s capacity purchase, according to the Adjustment Period COP and Trades Snapshot for the hour that includes the 15-minute Settlement Interval. |
| RUCCSADJq,h | MW | RUC Capacity Sale at Adjustment Period—The QSE q’s capacity sale, according to the Adjustment Period COP and Trades Snapshot for the hour that includes the 15-minute Settlement Interval. |
| DAEPq,p,h | MW | Day-Ahead Energy Purchase—The QSE q’s energy purchased in the DAM at the Settlement Point p for the hour that includes the 15-minute Settlement Interval. |
| DAESq,p,h | MW | Day-Ahead Energy Sale—The QSE q’s energy sold in the DAM at the Settlement Point p for the hour that includes the 15-minute Settlement Interval. |
| RTQQEPSNAPq,p,i | MW | QSE-to-QSE Energy Purchase by QSE by point—The QSE q’s Energy Trades in which the QSE is the buyer at the delivery Settlement Point p for the 15-minute Settlement Interval, in the COP and Trades Snapshot. |
| RTQQESSNAPq,p,i | MW | QSE-to-QSE Energy Sale by QSE by point—The QSE q’s Energy Trades in which the QSE is the seller at the delivery Settlement Point p for the 15-minute Settlement Interval, in the COP and Trades Snapshot. |
| RTQQEPADJq,p,i | MW | QSE-to-QSE Energy Purchase by QSE by point—The QSE q’s Energy Trades in which the QSE is the buyer at the delivery Settlement Point p for the 15-minute Settlement Interval, in the last COP and Trades Snapshot at the end of the Adjustment Period for that Settlement Interval. |
| RTQQESADJq,p,i | MW | QSE-to-QSE Energy Sale by QSE by point—The QSE q’s Energy Trades in which the QSE is the seller at the delivery Settlement Point p for the 15-minute Settlement Interval, in the last COP and Trades Snapshot at the end of the Adjustment Period for that Settlement Interval. |
| q | none | A QSE. |
| p | none | A Settlement Point. |
| r | none | A Generation Resource that is QSE-committed or RUC-decommitted (subject to paragraphs (1) and (2) above) for the Settlement Interval. |
| z | none | A previous RUC process for the Operating Day. |
| i | none | A 15-minute Settlement Interval. |
| h | none | The hour that includes the Settlement Interval i. |
| ruc | none | The RUC process for which this RUC Shortfall Ratio Share is calculated. |

5.7.4.1.2	RUC Capacity Credit

A QSE that is charged for a capacity shortfall in one RUC process gets a capacity credit equal to the minimum of the QSE’s RUC shortfall (MW) or the total RUC capacity purchased multiplied by the QSE’s shortfall ratio share.  The capacity credit to be used in future RUC processes for the same 15-minute Settlement Interval is calculated as follows:

RUCCAPCREDITruc,i,q	=	Min [RUCSFruc,i,q, (RUCCAPTOTruc,h* RUCSFRSruc,i,q)]

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| RUCCAPCREDITruc,i,q | MW | RUC Capacity Credit by QSE—The capacity credit resulting from capacity paid through the RUC Capacity-Short Charge for the 15-minute Settlement Interval. |
| RUCSFruc,i,q | MW | RUC Shortfall—The QSE’s capacity shortfall for the RUC process for the 15-minute Settlement Interval. |
| RUCSFRSruc,i,q | none | RUC Shortfall Ratio Share—The ratio of the QSE’s capacity shortfall to the sum of all QSEs’ capacity shortfalls, for the RUC process, for the 15-minute Settlement Interval. |
| RUCCAPTOTruc,h | MW | RUC Capacity Total—The total capacity of all RUC-committed Resources during the RUC process, for the hour that includes the 15-minute Settlement Interval. |
| q | none | A QSE. |
| i | none | A 15-minute Settlement Interval. |
| h | none | The hour that includes the Settlement Interval i. |
| ruc | none | The RUC process for which this RUC Capacity Credit is calculated. |

5.7.4.2	RUC Make-Whole Uplift Charge

If the revenues from the charges under Section 5.7.4.1, RUC Capacity-Short Charge, are not enough to cover all RUC Make-Whole Payments, including amounts for RMR Units, for a 15-minute Settlement Interval, then the difference will be uplifted to all QSEs on a Load Ratio Share basis, as a RUC Make-Whole Uplift Charge, calculated as follows:

LARUCAMTq,i	=	(-1) * ( RUCMWAMTTOTh / 4 + RUCCSAMTTOTi) * LRSq,i

Where:

RUCMWAMTTOTh 		=	ΣrucRUCMWAMTRUCTOTruc,h

RUCCSAMTTOTi	    	 =	ΣrucΣqRUCCSAMTruc,i,q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| LARUCAMTq,i | $ | RUC Make-Whole Uplift Charge—The amount owed from the QSE based on Load Ratio Share, for the 15-minute Settlement Interval. |
| RUCMWAMTTOTh | $ | RUC Make-Whole Amount Total—The sum of RUC Make-Whole Payments for all RUC processes, including amounts for RMR Units, for the hour that includes the 15-minute Settlement Interval. |
| RUCMWAMTRUCTOTruc,h | $ | RUC Make-Whole Amount Total per RUC—The sum of RUC Make-Whole Payments for a particular RUC process, including payments for RMR Units, for the hour that includes the 15-minute Settlement Interval. |
| RUCCSAMTTOTi | $ | RUC Capacity Amount Total—The sum of RUC Capacity-Short Charges for all QSEs and RUC processes, including payments for RMR Units, for the 15-minute Settlement Interval. |
| RUCCSAMTruc,i,q | $ | RUC Capacity-Short Amount—The charge to a QSE, due to capacity shortfall for a particular RUC process, for the 15-minute Settlement Interval. |
| LRSq,i | none | Load Ratio Share—The ratio of Adjusted Metered Load to the total ERCOT Adjusted Metered Load for the 15-minute Settlement Interval. See Section 6.6.2, Load Ratio Share, item (2). |
| i | none | A 15-minute Settlement Interval. |
| h | none | The hour that includes the Settlement Interval i. |
| ruc | none | A RUC Process. |
| q | none | A QSE. |

5.7.5	RUC Clawback Payment

ERCOT shall pay the revenues from all RUC Clawback Charges, including amounts for RMR Units, in a 15-minute Settlement Interval to all QSEs, on an LRS basis, as the RUC Clawback Payment.  The RUC Clawback Payment is calculated as follows for each QSE for each 15-minute Settlement Interval:

LARUCCBAMTq,i	=	(-1) * (RUCCBAMTTOTh / 4 * LRSq,i)

Where:

RUCCBAMTTOTh	=	ΣqΣrRUCCBAMTq,r,h

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| LARUCCBAMTq,i | $ | RUC Clawback Payment—The RUC make-whole clawback payment to a QSE to uplift RUC Make-Whole Clawback Charges received, for a 15-minute Settlement Interval. |
| RUCCBAMTTOTh | $ | RUC Clawback Charge Total —The sum of RUC Clawback Charges to all QSEs, including amounts for RMR Units, for the hour that includes the 15-minute Settlement Interval. |
| LRSq,i | none | Load Ratio Share—The LRS for the 15-minute Settlement Interval. See Section 6.6.2, Load Ratio Share. |
| RUCCBAMTq,r,h | $ | RUC Clawback Charge—The RUC Clawback Charge to the QSE q for the Resource r, for the hour that includes the 15-minute Settlement Interval. When one or more Combined Cycle Generation Resources are committed by RUC, a charge is made to the Combined Cycle Train for all RUC-committed Combined Cycle Generation Resources. |
| q | None | A QSE. |
| i | none | A 15-minute Settlement Interval. |
| h | none | The hour that includes the Settlement Interval i. |
| r | none | A RUC-committed Generation Resource. |

5.7.6	RUC Decommitment Charge

ERCOT shall charge each QSE a RUC Decommitment Charge, on an LRS basis, all revenues paid as a result of RUC Decommitment Payments, including amounts for RMR Units.  The RUC Decommitment Charge for a 15-minute Settlement Interval is calculated as follows:

LARUCDCAMTq,i	=	(-1) * [(RUCDCAMTTOTh / 4) * LRSq,i]

Where:

RUCDCAMTTOTh	=	ΣqΣrRUCDCAMTq,r,h

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| LARUCDCAMTq,i | $ | RUC Decommitment Charge—The RUC Decommitment Charge to a QSE, for a 15-minute Settlement Interval. |
| RUCDCAMTTOTh | $ | RUC Decommitment Charge Total—The sum of RUC Decommitment Payments to all QSEs, including amounts for RMR Units, for the hour that includes the 15-minute Settlement Interval. |
| LRSq,i | none | Load Ratio Share—The LRS for the 15-minute Settlement Interval. See Section 6.6.2, Load Ratio Share. |
| RUCDCAMTq,r,h | $ | RUC Decommitment Charge—The RUC Decommitment Charge to the QSE q for the Resource r, for the hour that includes the 15-minute Settlement Interval. When one or more Combined Cycle Generation Resources are decommitted by RUC, payment is made to the Combined Cycle Train for all RUC-decommitted Combined Cycle Generation Resources. |
| q | None | A QSE. |
| i | none | A 15-minute Settlement Interval. |
| h | none | The hour that includes the Settlement Interval i. |
| r | None | A RUC-decommitted Generation Resource. |