## Slide 1: Summary of the CREZ Reactive Study
Warren Lasher
Manager, Long-Term Planning and Policy

## Slide 2: Project Overview
The CREZ Reactive Study had three major work areas:
  Determine design specifications of CREZ series compensation
  Provide location, size and response requirements of shunt compensation
  Evaluate potential impacts of sub-synchronous interactions with transmission equipment
CREZ Reactive Study was managed in a joint effort by ERCOT and the CREZ TSPs
The study was conducted by a team of consultants from ABB, Inc.

## Slide 3: Study Input Assumptions
Three steady-state AC cases were initially developed
  Maximum Exports (High wind, low load)
  Minimum Exports (Low wind, low load)
  Peak Load
  Max Edison case was later developed to stress southern portion of the CREZ system (High central and southern CREZ wind, low load)
Cases contain incremental CREZ wind (from CREZ Transmission Study) and generation units that are operational or have a signed interconnection agreement
As details of the CREZ transmission system were changed, the cases were updated (new conductor types, line lengths, etc.)
New CREZ wind was assumed to be 85% Type III turbines (GE 1.5 MW) and 15% Type II turbines (Vestas V80 1.8 MW).
Dynamic load models were developed by the TSPs and ABB

## Slide 4: Initial Stability Results
Initial simulations indicated the presence of two sources of instability: small signal and large signal.
Graphical representation of oscillatory (small signal) behavior
These results are indicative of power electronics interactions due to low system strength

## Slide 5: System Strength Considerations
Short Circuit Ratio (SCR) describes the system strength (a.k.a. small-signal fundamental-frequency source impedance) at a particular point in the network with respect to the corresponding amount of nearby wind power generation:
The impacts of low SCR (in areas with no existing synchronous generation) on large numbers of installations of power-electronics based devices (like wind turbine inverters) is relatively unknown in the industry. The extent to which the available wind turbine dynamic models accurately describe the physical impacts of low SCR is uncertain.
Several potential solutions appear to exist; however, the cost-effectiveness of potential solutions to the problem of low system strength needs to be evaluated with new software tools that accurately reflect the impacts of low SCR.

## Slide 6: Initial Build Case
 | CTOS | Minimum Exports | Initial Build | Maximum Exports
Wind Installed Capacity MW | 18,455 | 21,958 | 17,517 | 21,958
Wind Dispatched Level MW | 12,975 | 2,562 | 12,802 | 15,430
Other Generation Dispatched MW | 21,725 | 37,317 | 27,646 | 25,534
Comparison of Generation Levels in the CREZ Transmission Optimization Study (CTOS) and CREZ Steady-State Reactive Cases
The Initial Build Case was developed to evaluate the reactive equipment needed to support the estimated potential wind development that could occur without devices to supplement system strength.
  Initial Build strategy will provide flexibility to adjust the reactive plan to meet evolving system needs
  Will also provide additional time for analysis of system strength implications and evaluation of cost-effective of solution(s)

## Slide 7: Reactive Device Recommendations
The following capacitive devices are being recommended based on analysis of the Initial Build Case:
Station | Shunt Capacitors (MVAr) | SVC (MVAr)
RILEY | 316 | 
KRUM | 50 | 
TESLA |  | +300 (-100)
EDITH CLARKE |  | 
SILVERTON |  | 
COTTON |  | 
SCURRY | 100 | 
WEST SHACKLEFORD |  | 
GRELTON | 50 | 
BROWN | 200 | 2 x [+300 (-100)]
KILLEEN | 100 | 
BIG HILL | 144 | 
PARKER |  | +300 (-100)
HAMILTON |  | +200 (-50)
In addition, ~-4,000 MVArs of shunt static inductive devices will be required, at 30 substations, for voltage control under low wind conditions and for line maintenance and operations.
Estimated costs:
Shunt Capacitors: ~$25 M
SVCs: ~$150 M
Shunt Reactors: ~$220 M

## Slide 8: Sub-Synchronous Interaction Analysis
Several different potential issues associated with use of power electronics on transmission systems:
  Sub-synchronous Resonance (SSR) – primarily a concern for large synchronous generation units
    Potential impacts to 6 existing generations units were evaluated (Comanche Peak, Tradinghouse, Willow Creek, Oklaunion, Hays, Odessa)
  Sub-synchronous Torsional Interactions (SSTI) – results from operation of power electronics devices near large synchronous generation units
    Study results indicate this should not be a significant issue
  Sub-synchronous Interactions (SSI) – impacts to wind turbine generators due to interaction between electrical resonance and power electronic converter controls
    There are transmission system and unit-specific mitigation options

## Slide 9: Geography of SSI
Locations most prone to have Sub-Synchronous Interaction (for Type 3 turbines):
West Shackelford – SSI with no contingencies
Dermott – SSI after 1 contingency
Big Hill – SSI after 1 contingency
Locations directly connected to a compensated line or potentially in a radial or semi-radial configuration following the outage of one or a few nearby circuits will be SSI prone.

## Slide 10: Conclusions
ERCOT will recommend installation of the reactive devices specified through analysis of the Initial Build, Minimum Exports, and Peak Load cases
  Maintain flexibility to adjust location and size of dynamic reactive devices to reflect actual development of wind generation and other changes to the transmission grid
  Allows maximum wind development possible before selecting cost-effective solution(s) to low system strength conditions
Reactive devices in the Maximum Exports/Max Edison cases represent potential requirements for the full CREZ build-out. Cost-effectiveness of this solution is not known at this time.
Further study needed:
  Identify new tool and conduct studies of potential solutions to system strength issue
  Modifications to Generation Interconnection requirements/process to reflect need for additional SSI studies
  Evaluation of options for SSR/SSI mitigation

## Slide 11
CREZ Reactive Study
Questions?