| NOGRR Number | 044 | NOGRR Title | Clarification of a PSS In-Service |
| --- | --- | --- | --- |

| Date | January 11, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Adrianne Brandt |
| E-mail Address | Adrianne.brandt@austinenergy.com |
| Company | City of Austin d/b/a Austin Energy |
| Phone Number | 512.505.3749 |
| Cell Number | 512.799.9517 |
| Market Segment | Municipally Owned Utility (IOU) |

Comments

Austin Energy (AE) submits these comments to proposed revisions to Nodal Operating Guide Revision Request (NOGRR) 044, Clarification of a PSS In-Service.  AE is concerned that the current proposed language introduces inconsistencies, ambiguities and a potential new requirement as summarized below.

- Section 2.2.6, paragraph (1) says that “Generation Resources with Power System Stabilizers (PSSs) shall keep their PSSs in-service (“On” or energized) at all times the generator is synchronized to the ERCOT Transmission Grid.”

- Section 2.2.6, paragraph (4)(a)(ii) says, for Synchronous Generation Resources greater than 10 MW installed on or before January 1, 2008, a Generation Resource shall notify ERCOT “whether or not PSS settings have been determined and the PSS has been or will be placed in-service.”

Essentially, paragraph (1) ignores the situation where a PSS is installed but has not been placed in-service, which is clearly allowed by paragraph (4)(a)(ii) for certain Generation Resources.  AE’s proposed change alleviates the above contradiction.

Please note that AE has made its proposed language changes on the comments submitted by ERCOT January 10, 2011.

| Overall Market Benefit | Removes inconsistent language. |
| --- | --- |
| Overall Market Impact | None |
| Consumer Impact | None |

Revised Cover Page Language

| NOGRR Number | 044 | NOGRR Title | Clarification of a PSS In-Service and Improved Communication Process for Changes in PSS Status. |
| --- | --- | --- | --- |

| Guide Section Requiring Revision | 2.2.5, Automatic Voltage Regulators 2.2.6, Power System Stabilizers |
| --- | --- |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) clarifies that a Power System Stabilizer (PSS) must be “On” and in an active MW range to be considered in service. |
| Reason for Revision | It is currently perceived that a PSS is deemed to be in service when a generator is On-Line and synchronized to the ERCOT Transmission Grid. However, that may not always be the case. For example, a PSS can be turned on or off via a control switch. Furthermore, if the PSS is turned on, it does not become active or responsive until the MW level surpasses the unit stability limit as it increases in MWs from zero MWs after synchronization to the ERCOT Transmission Grid. In the decreasing MW mode it will de-activate when it surpasses the defined low stability limit while synchronized to the ERCOT Transmission Grid. The proposed revisions mitigate these concerns. |

Revised Proposed Guide Language

- 2.2.5	Automatic Voltage Regulators

(1)	Generation Entities shall notify their QSEs of any change in AVR status (e.g. AVR unavailability due to maintenance or failure and when the AVR returns to normal operation).  QSEs shall notify ERCOT and its TO of any change in AVR status and shall supply AVR status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.

(2)	Generation Entities shall conduct performance tests on AVRs or verify AVR performance through comparison with operational data a minimum of every five years as prescribed in item (5) of Protocol Section 8.1.1.2.1.4, Voltage Support Service (VSS) Qualification, or if equipment characteristics are knowingly modified, within 30 days of the modification.  The test reports should include the minimum and maximum excitation limiters, volts/hertz settings, gain and time constants, type of voltage regulator control function, date tested, and voltage regulator control setting.

(3)	Generation Resources shall verify excitation systems model data upon initial installation, within 30 days of performance modifications, and a minimum of five years thereafter.

(4)	Generation Resource AVR modeling information required in the ERCOT Planning Criteria shall be determined from actual Generation Resource testing described in these Operating Guides.  Within 30 days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the Transmission Service Provider (TSP).

2.2.6	Power System Stabilizers

- Generation Resources with  Power System Stabilizers (PSSs) shall keep their PSSs in-service (“On” or energized and performing as designed by the manufacturer) unless the PSS is installed but not in service as described in paragraph (4)(a)(ii) below.  When available, the PSS shall be active and responsive at all times the generator is synchronized to the ERCOT Transmission Grid and operating at or above its Low Sustained Limit (LSL).

- Generation Entities shall notify their QSEs of any change in PSS status (e.g. PSS unavailability due to maintenance or failure and when the PSS returns to normal operation).  QSEs shall notify ERCOT and its TO of any change in PSS status and shall supply PSS status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.

- Synchronous Generation Resources greater than 10 MW installed between January 1, 2008 and the Texas Nodal Market Implementation Date shall install a PSS and place the PSS in service within 180 days after the Texas Nodal Market Implementation Date.  Synchronous Generation Resources greater than 10MW installed after the Texas Nodal Market Implementation Date shall install a PSS and place the PSS in-service prior to the commercial operation start date of the Generation Resource.  The Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- Synchronous Generation Resources greater than 10 MW installed before January 1, 2008 are subject to the following requirements:

(a)	All Generation Resources that are in this category shall notify ERCOT and the TSP:

(i)	Whether or not a PSS has been installed; and

(ii)	Whether or not PSS settings have been determined and the PSS has been 	or will be placed in-service.

(b)	If a PSS was in-service prior to January 1, 2008 the PSS shall remain in-service with the established PSS settings, provided that ERCOT may direct the Generation Resource  to modify the settings.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.

(c)	If a PSS is newly installed and/or placed in-service the Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- If an excitation system on a synchronous Generation Resource greater than 10 MW is modified or replaced after January 1, 2008, the Generation Resource shall install a PSS, establish PSS settings to dampen modes with oscillations within the range of 0.2 to 2.0 Hz, and place the PSS in-service.  The settings shall be tested and tuned to ensure the excitation system has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- If it is determined that a change in PSS settings or the addition of a PSS to a synchronous Generation Resource would improve overall system performance, ERCOT shall coordinate with the Generation Resource owner to determine appropriate settings.  Within 180 days of determining appropriate settings, the Generation Resource owner shall revise the PSS setting and/or install the PSS.  Any PSS setting established pursuant to this section shall be established to dampen modes with oscillations as directed by ERCOT and place the PSS in-service.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- At least every five years, Generation Entities shall conduct performance tests on PSS settings or verify PSS performance based on operational data.  If PSS equipment characteristics are modified, the Generation Entity shall conduct a performance test within 30 days of the modification.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date

- The results of PSS tests or PSS performance verification shall be supplied to ERCOT and the TSP within 30 days of a request from ERCOT.