## Slide 1: PDCWG Report to ROS
December 9, 2010
Sydney Niemeyer

## Slide 2
CPS1 = 147.39

## Slide 8
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 151.3

## Slide 12
Same 600 MW unit MW movement due to frequency each year.

## Slide 13: ERCOT Total Load and Wind Generation
Data source not EPS quality.
Confidence in data is good with some telemetry errors scrubbed.
Next three slides for reference only.

## Slide 17: PDCWG Meeting Dec 8, 2010
Frequency Event review
  November 7, 2010 01:57 Resource trip 523 MW
    Excellent Interconnection frequency response.
    Maximum frequency rate of change was -0.066 Hz/second.
    WGR energy was 15.93% of total energy.
  November 8, 2010 13:58 Resource trip 709 MW
    Frequency response at B+30 was below 420 MW/0.1 Hz minimum at 398 MW/0.1 Hz.
    Maximum frequency rate of change was -0.074 Hz/second.
    WGR energy was 8.87% of total energy.
    There was some frequency response that was not sustained by the Resources and some spinning reserve that was not frequency responsive.
  November 25, 2010 04:30 High frequency
    1623 MW of WGR increase in 23 minutes and 16 seconds.
  December 3, 2010 00:04 Low frequency
    Approximately 1900 MW of Generation shutdown.
PDCWG Scope revision will be requested at the January ROS meeting.
  Since Resource Entities are now evaluated individually by GREDP and Base Point Deviation, the PDCWG believes they should be allowed to be members of the PDCWG. This is the only change to the scope so far.
PDCWG meeting dates for 2011 have been set and are at least 8 days before the expected ROS meetings.