ERCOT Operations Report

Dec 2010 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 12/3/2010 0:03 | 59.869 | 155 | Expected Gen Deviation -1970 MW in 12 mins; out of URS |
| 12/5/2010 21:10 | 59.871 | 6 | Unit trip with 392 MW |
| 12/6/2010 11:25 | 59.811 | 28 | Unit trip with 760 MW |
| 12/9/2010 17:34 | 59.805 | 92 | Unit trip with 751 MW |
| 12/11/2010 22:38 | 59.803 | 40 | Unit trip with 574 MW |
| 12/11/2010 23:38 | 59.749 | 188 | Unit trip with 1071 MW |
| 12/14/2010 4:57 | 60.103 | 84 | out of DRS |
| 12/15/2010 18:08 | 60.144 | 181 | Non-spin units coming online, Expected Gen Deviation +1500 MW in 3 min |
| 12/16/2010 6:15 | 59.780 | 364 | Unit trip with 775 MW |
| 12/16/2010 15:16 | 59.822 | 36 | Unit trip with 818 MW |
| 12/17/2010 17:27 | 59.852 | 40 | Unit trip with 646 MW |
| 12/19/2010 2:39 | 59.823 | 96 | Unit trip with 810 MW |
| 12/19/2010 15:56 | 59.843 | 8 | Unit trip with 586 MW |
| 12/19/2010 20:18 | 59.781 | 108 | Unit trip with 983 MW |
| 12/21/2010 22:02 | 59.753 | 474 | Expected Gen Deviation -2500 MW in 3 mins due to numerous units status change to ONTEST during shut-down process; out of URS |
| 12/22/2010 4:44 | 60.175 | 630 | Expected Gen Deviation +1000 MW in 4 min. Out of DRS |
| 12/23/2010 14:41 | 59.842 | 8 | Unit trip with 553 MW |
| 12/24/2010 16:15 | 59.814 | 27 | Expected Gen Deviation -2000 in 2s |
| 12/26/2010 8:32 | 59.827 | 32 | Unit trip with 820 MW |
| 12/28/2010 4:56 | 60.122 | 240 | Expected Gen Deviation +800 MW in 3 min; out of DRS |
| 12/29/2010 0:00 | 59.879 | 216 | Units coming offline across 2400, Expected Gen Deviation -1100 MW in 5 min; out of URS |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 12/21/10 22:05:02 | 12/21/10 22:12:07 | 0:07:05 | 290.3 |  |

RUC Capacity Purchases

| Details | Unit Days |
| --- | --- |
| COAST | 8 |
| EAST | 3 |
| FAR WEST | 56 |
| NORTH CENTRAL | 4 |
| SOUTH | 13 |
| SOUTH CENTRAL | 13 |
| WEST | 1 |
| Grand Total | 98 |

SCED Congestion Management Activity Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Moss Switch - Holt Switch 138kV | Odessa North - Odessa Basin Switch 138kV | 14 |
| W.A. Parish - O'brien 345kV | Garrott - Midtown 138kV | 6 |
| Basecase | Syntex - Syntex Tap 69kV | 5 |
| Basecase | Matador - Paducah 69kV | 4 |
| Basecase | Naval Base - North Padre 69kV | 4 |
| Basecase | Golden Switch - Brand TU 138kV | 3 |
| Basecase | Spur 138/69kV AXFMR1 | 3 |
| Willow Valley Switch - Bluff Creek Switch 138kV | Ackerly Vealmoor Sw - Ackerly 69kV | 3 |
| Cagnon - Marbach 138kV | West Side - Five Points 138kV | 3 |
| Basecase | Nelson Sharpe PS | 2 |
| Basecase | Notrees - Notrees Switch 138kV | 2 |
| Basecase | Victoria - Thomaston 138kV | 2 |
| Basecase | Odessa North 138/69kV AXFMR1 | 2 |
| Hearne 138/69kV AT1 | Hilltop Lakes 138/69kV AT1 | 2 |
| Airline - Westside 138kV | Nelson Sharpe PS | 2 |
| Cagnon 345/138kV AXFMR3 | Med Center - Hamilton Wolfe 138kV | 2 |
| Willow Valley Switch - Lamesa 138kV | Ackerly Vealmoor Sw - Ackerly 69kV | 2 |
| Garfield - Hicross & Onion - Pilot Knob 138kV | Garfield - Onion 138kV | 2 |
| Basecase | Barney Davis - Woolridge 138kV | 1 |
| Austrop - Sandow Switch 345kV | Gilleland - McNeil LCRA 138kV | 1 |
| Basecase | Round Rock - Round Rock NE 138kV | 1 |
| Aspermont - Spur 138kV | Matador - Paducah 69kV | 1 |
| China Grove Switch - Snyder 138kV | Golden Switch - Brand TU 138kV | 1 |
| Lamesa - Andrews North 138kV | Stanton Switch - Midland East 138kV | 1 |
| Bell County - Temple Switch 138kV | Seaton 138/69kV AT1 | 1 |
| Moss Switch - Odessa EHV Switch 138kV | Holt Switch - Ector Shell Tap 69kV | 1 |
| China Grove Switch - Morgan SES 138kV | China Grove Switch - Morgan SES 138kV | 1 |
| STP - Whitepoint & Hillje 345kV | Blessing - Lolita 138kV | 1 |
| Austrop - Lost Pines 345kV | Salem 345/138kV AT3 | 1 |
| Barney Davis - Airline & Rodd Field 138kV | Nelson Sharpe PS | 1 |
| Graham SES - Long Creek & Cook Field 345kV | Murray - Paint Creek 138kV | 1 |
| Nueces Bay - Koch Upriver & Lon Hill 138kV | Hiway 9 - Air Liquid AEP 69kV | 1 |
| Basecase | McKenzie - Westside 138kV | 1 |
| Watermill - Tricorner & Trinidad 345kV | Trinidad 345/138kV AXFMR6 | 1 |
| Pearsall - San Miguel 138kV | Pearsall - Big Foot Sub 69kV | 1 |
| Basecase | Pearsall 138/69kV AXFMR4 | 1 |
| Cagnon - Calaveras & Braunig 345kV | Med Center - Hamilton Wolfe 138kV | 1 |
| Garfield - Onion & Hicross 138kV | Lytton Springs - Pilot Knob 138kV | 1 |
| Farmersville - Monticello SES 345kV | Monticello SES - Monticello Mining 138kV | 1 |
| La Palma - Laureles 138KV | La Palma - Villa Cavazos 138KV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 25 |
| Valley Import | 1 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

Stanton Modified

Mount Enterprise Energized (Dec 13)

Stryker Creek Approved not energized

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 12/15/2010 | Nodal Resource Desk V1 Rev2 | 513 |
| 12/15/2010 | Nodal Real Time Desk V1 Rev2 | 512 |
| 12/15/2010 | Nodal Transmission and Security Desk V1 Rev2 | 511 |
| 12/15/2010 | Nodal Reliability Unit Commitment Desk V1 Rev2 | 510 |
| 12/01/2010 | Nodal Transmission and Security Desk V1 Rev 1 | 509 |
| 12/01/2010 | Nodal Shift Supervisor Desk V Rev 1 | 508 |
| 12/01/2010 | Nodal Resource Desk V1 Rev 1 | 507 |
| 12/01/2010 | Nodal Reliability Unit Commitment Desk V1 Rev 1 | 506 |
| 12/01/2010 | Nodal Real Time Desk V1 Rev 1 | 505 |
| 12/01/2010 | Nodal DC Tie Desk V1 Rev 1 | 504 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

12/10 19:39	ERCOT declared an Emergency due to the failure of the SCED process.

12/11 20:40   	ERCOT declared an Emergency due to the failure of the SCED process.

12/27 05:45	ERCOT declared an Emergency due to the failure of the SCED process, starting at 16:55

Communication Issues

None

## ERCOT peak (Unofficial)

12/13 08:00 44,376 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2007 | 2008 | 2009 | 2010 |
| January | 4.55 | 3.30 | 4.11 | 3.78 |
| February | 3.75 | 3.59 | 3.49 | 3.79 |
| March | 2.70 | 3.29 | 3.24 | 2.24 |
| April | 3.00 | 2.45 | 2.66 | 2.47 |
| May | 3.22 | 3.01 | 2.90 | 2.63 |
| June | 4.46 | 2.81 | 2.89 | 2.84 |
| July | 4.29 | 2.55 | 2.83 | 2.39 |
| August | 3.11 | 3.66 | 3.07 | 2.29 |
| September | 3.78 | 4.99 | 3.68 | 3.14 |
| October | 3.08 | 2.79 | 2.92 | 2.37 |
| November | 2.95 | 2.60 | 1.93 | 3.46 |
| December | 3.74 | 4.54 | 3.70 | 2.60 |
| Annual Average | 3.55 | 3.29 | 3.11 | 2.83 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 12/4/2010 | 17:53 | ERCOT issued an Advisory due to Physical Reserve Capability (PRC) below 3000 MW. |
| 12/5/2010 | 5:30 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 12/6/2010 | 17:57 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 12/9/2010 | 21:12 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 12/10/2010 | 5:10 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 12/12/2010 | 19:30 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 12/15/2010 | 16:44 | ERCOT issued an OCN for projected reserve capacity shortage for HE 1900-2100. |
| 12/15/2010 | 17:44 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 12/16/2010 | 11:01 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 12/18/2010 | 5:10 | ERCOT issued an OCN for a projected reserve capacity shortage for HE 10:00 -13:00. |
| 12/21/2010 | 2:11 | ERCOT issued an OCN for a projected reserve capacity shortage for H.E. 1200 - 1500 and 1800 - 2200 |
| 12/21/2010 | 9:45 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 12/22/2010 | 11:06 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 12/23/2010 | 2:46 | ERCOT issued an OCN issued for projected reserve capacity shortage for HE 11:00. |
| 12/23/2010 | 4:20 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 12/25/2010 | 6:57 | ERCOT issued an OCN for projected reserve capacity shortage for H.E. 1100 and 1200 and 1900 through 2300. |
| 12/25/2010 | 18:39 | ERCOT issued Advisory due to PRC below 3000 MW. |
| 12/26/2010 | 0:07 | ERCOT issued an OCN for projected reserve capacity shortage for hrs 09:00 - 1400. |
| 12/30/2010 | 9:30 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 12/31/2010 | 10:07 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 12/31/2010 | 16:20 | ERCOT issued an OCN for projected reserve capacity shortage for HE 19-20. |

Transmission Watch

None

Emergency Notice

12/10 19:39	ERCOT declared an Emergency due to the failure of the SCED process.

12/11 20:40   	ERCOT declared an Emergency due to the failure of the SCED process.

12/27 05:45	ERCOT declared an Emergency due to the failure of the SCED process, starting at 16:55

Texas RE Event Analysis

12/11 23:38	Simultaneous loss of multiple units for a total of 1071 MW of generation caused a frequency deviation of 0.251 Hz (59.749 Hz) and the deployment of 203 MW of Hydro supplying Responsive Reserve. System frequency recovered to 60 Hz in approximately 6 minutes and 56 seconds.

12/14 06:17	Monticello Mining SPS #25 activated. There is no evidence that the Monticello Mining SPS #25 SPS failed to operate as designed.

12/19 08:06	Monticello Mining SPS #25 activated. Still under investigation.

12/30 07:07	Stanton Switch Station SPS #46 activated. Still under investigation.

Others

None