| NOGRR Number | 052 | NOGRR Title | Conductor/Transformer Transmission Facility Rating |
| --- | --- | --- | --- |
| Date |  | January 24, 2011 |  |
| Submitters’ Information |  |  |  |
| Name |  | Jay Teixeira |  |
| E-mail Address |  | jteixeira@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | (512) 248-6582 |  |
| Cell Number |  |  |  |
| Market Segment |  | N/A |  |

Comments

ERCOT submits these comments to remove the Transmission Element Ratings definitions from the Operating Guides.  Removing these definitions will eliminate potential conflict with the Protocols as these Ratings are currently defined in Section 2.1, Definitions.  ERCOT will sponsor a Nodal Protocol Revision Request (NPRR) to add the definition of Conductor/Transformer Rating to the Protocols.

Revised Proposed Guide Language Revision

- 3.9.4	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the Rating of their Facilities and shall send the methodology used to ERCOT  in accordance with paragraph (3) of Protocol Section 3.10, Network Operations Modeling and Telemetry.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide to ERCOT all nominal Transmission Element Ratings.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Element to within Normal Ratings as soon as practicable, based on Good Utility Practice.