| NOGRR Number | 044 | NOGRR Title | Clarification of a PSS In-Service and Improved Communication Process for Changes in PSS Status (formerly “Clarification of a PSS In-Service”) |
| --- | --- | --- | --- |
| Timeline | Normal | Action | Approved |
| Date of Decision |  | February 3, 2011 |  |
| Proposed Effective Date |  | March 1, 2011 |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Guide Sections Requiring Revision |  | 2.2.5, Automatic Voltage Regulators 2.2.6, Power System Stabilizers |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) clarifies that a Power System Stabilizer (PSS) must be “On” and in an active MW range to be considered in service. This NOGRR also proposes language changes to improve the communication process for any change in PSS status. |  |
| Reason for Revision |  | It is currently perceived that a PSS is deemed to be in service when a generator is On-Line and synchronized to the ERCOT Transmission Grid. However, that may not always be the case. For example, a PSS can be turned on or off via a control switch. Furthermore, if the PSS is turned on, it does not become active or responsive until the MW level surpasses the unit stability limit as it increases in MWs from zero MWs after synchronization to the ERCOT Transmission Grid. In the decreasing MW mode it will de-activate when it surpasses the defined Low Sustained Limit (LSL) while synchronized to the ERCOT Transmission Grid. The proposed revisions mitigate these concerns. |  |
| Overall Market Benefit |  | No monetary benefit. However, a better clarity as to the actual PSS serviceable range. |  |
| Overall Market Impact |  | None. |  |
| Consumer Impact |  | None. |  |
| Procedural History |  | - On 6/3/10, NOGRR044 and the associated CEO Revision Request Review were posted. - On 7/19/10, ERCOT comments were posted. - On 7/21/10, the Operations Working Group (OWG) considered NOGRR044. - On 8/2/10, an Impact Analysis was posted. - On 8/18/10, the OWG considered the 7/21/10 OWG Recommendation Report and Impact Analysis for NOGRR044. - On 9/23/10, OWG again considered NOGRR044. - On 10/20/10, OWG again considered NOGRR044. - On 12/15/10, OWG again considered NOGRR044. - On 1/10/11, a second set of ERCOT comments were posted. - On 1/11/11, Austin Energy comments were posted. - On 1/12/11, Luminant comments were posted. - On 1/13/11, ROS considered NOGRR044. - On 1/19/11, a third set of ERCOT comments were posted. - On 1/25/11, STEC comments were posted. - On 2/1/11, a second set of Luminant comments were posted. - On 2/3/11, TAC considered NOGRR044. |  |
| OWG Decision |  | On 7/21/10, OWG was in consensus to recommend approval of NOGRR044 as amended by the 7/19/10 ERCOT comments and as revised by OWG. On 8/18/10, OWG was in consensus to table NOGRR044 for one month. On 9/23/10, OWG was in consensus to table NOGRR044 for one month. On 10/20/10, OWG was in consensus to table NOGRR044 for one month. On 12/15/10, OWG was in consensus to endorse and forward the 7/21/10 OWG Recommendation Report as revised by OWG and the Impact Analysis for NOGRR044 to ROS. |  |
| Summary of OWG Discussion |  | On 7/21/10, ERCOT Staff recommended the addition of changes proposed in Section 2.2.6 by NOGRR041, Synchronization of Section 2 with Nodal Protocols, to NOGRR044. On 8/18/10, it was requested that NOGRR044 be tabled for one month to allow time for manufacturers to review and comment. On 9/23/10, it was requested that NOGRR044 be tabled for one month to allow time for PSS vendors to review and comment. On 10/20/10, it was requested that NOGRR044 be tabled for one month to allow time for PSS vendors to review and comment. On 12/15/10, clarification was provided as a result of discussions between ERCOT and Market Participants that a PSS is required to be ON or energized and functioning as designed by the manufacturer. It was also noted Generation Resources with PSSs are required to notify ERCOT and the Transmission Service Provider (TSP) of any change in PSS status. |  |
| ROS Decision |  | On 1/13/11, ROS voted to recommend approval of NOGRR044 as amended by the 1/11/11 Austin Energy comments. There was one abstention from the Independent Power Marketer (IPM) Market Segment. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 1/11/11, the purpose of NOGRR044 was discussed. There was also discussion regarding the use of LSL versus “low stability limit” as a trigger for when a PSS must be active and responsive. It was noted that a unit’s stability is set by the conditions and not set by the manufacturer or the generator owner and that using low stability limit would be of concern since it is not defined in the Protocols. |  |
| TAC Decision |  | On 2/3/11, TAC unanimously voted to approve NOGRR044 as amended by the 2/1/11 Luminant comments and as revised by TAC. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 2/3/11, ERCOT Staff noted additional non-substantive changes to Section 2.2.6. |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None | None |
|  | 2 |  | 1.5 Full Time Equivalent (FTE) each for six Transmission and/or Distribution Service Providers (TDSPs) @ $65/hour |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Clarification of actual PSS engagement. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Jack Thormahlen |
| E-mail Address | Jack.thormahlen@lcra.org |
| Company | LCRA |
| Phone Number | 512-473-3200 ext 2635 |
| Cell Number |  |
| Market Segment | Cooperative |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 071910 | Proposed language changes to retain the 2008 dividing date for Generation Resources’ obligations with respect to PSS equipment and other clarifications. |
| ERCOT 011011 | Proposed language changes to revise the communication process for any change in PSS status. |
| Austin Energy 011111 | Proposed clarifying language changes to correct inconsistencies and alleviate contradiction in Operating Guide language regarding a potential new requirement. |
| Luminant 011211 | Proposed language changes to state that the PSS becomes active at the low stability limit and not the LSL. |
| ERCOT 011911 | Proposed language changes to remove references to “Texas Nodal Market Implementation Date” to clarify provisions related to PSS status. |
| STEC 012511 | Proposed language changes to clarify the communication process. |
| Luminant 020111 | Proposed language changes to accurately reflect that a PSS may become active at a level other than the LSL. |

Proposed Guide Language Revision

- 2.2.5	Automatic Voltage Regulators

(1)	Generation Entities shall notify their QSEs of any change in Automatic Voltage Regulator (AVR) status (e.g. AVR unavailability due to maintenance or failure and when the AVR returns to normal operation).  QSEs shall notify ERCOT and the TO at the Point of Interconnection (POI) of any change in AVR status and shall supply AVR status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.

(2)	Generation Entities shall conduct performance tests on AVRs or verify AVR performance through comparison with operational data a minimum of every five years as prescribed in item (5) of Protocol Section 8.1.1.2.1.4, Voltage Support Service (VSS) Qualification, or if equipment characteristics are knowingly modified, within 30 days of the modification.  The test reports should include the minimum and maximum excitation limiters, volts/hertz settings, gain and time constants, type of voltage regulator control function, date tested, and voltage regulator control setting.

(3)	Generation Resources shall verify excitation systems model data upon initial installation, within 30 days of performance modifications, and a minimum of five years thereafter.

(4)	Generation Resource AVR modeling information required in the ERCOT Planning Criteria shall be determined from actual Generation Resource testing described in these Operating Guides.  Within 30 days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the Transmission Service Provider (TSP).

2.2.6	Power System Stabilizers

- Generation Resources with  Power System Stabilizers (PSSs) shall keep their PSSs in-service (“On” or energized and performing as designed by the manufacturer) unless the PSS is installed but not in service as described in paragraph (4)(a)(ii) below.  When available, the PSS shall be active and responsive at all times the generator is synchronized to the ERCOT Transmission Grid and operating at or above its Low Sustained Limit (LSL).  However, if the PSS of a Generation Resource is set to be active and responsive at a point above the LSL for technical reasons, the Generation Resource may request ERCOT to allow an exception to the requirement that the PSS be active anytime the Generation Resource is at or above its LSL.  In order to obtain the exception, the Generation Resource shall notify ERCOT and provide the necessary technical information to ERCOT to justify a higher activation point for the PSS.

- Generation Entities shall notify their QSEs of any change in PSS status (e.g. PSS unavailability due to maintenance or failure and when the PSS returns to normal operation).  QSEs shall notify ERCOT and the TO at the POI of any change in PSS status and shall supply PSS status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.

- Synchronous Generation Resources greater than 10 MW installed after January 1, 2008 and on or before December 1, 2010 shall install a PSS and place the PSS in service by June 1, 2011.  Synchronous Generation Resources greater than 10MW installed after December 1, 2010 shall install a PSS and place the PSS in-service prior to the commercial operation start date of the Generation Resource.  The Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- Synchronous Generation Resources greater than 10 MW installed before January 1, 2008 are subject to the following requirements:

(a)	All Generation Resources that are in this category shall notify ERCOT and the TSP:

(i)	Whether or not a PSS has been installed; and

(ii)	Whether or not PSS settings have been determined and the PSS has been 	or will be placed in-service.

(b)	If a PSS was in-service prior to January 1, 2008, the PSS shall remain in-service with the established PSS settings, provided that ERCOT may direct the Generation Resource  to modify the settings.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.

(c)	If a PSS is newly installed and/or placed in-service the Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- If an excitation system on a synchronous Generation Resource greater than 10 MW is modified or replaced after January 1, 2008, the Generation Resource shall install a PSS, establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz, and place the PSS in-service.  The settings shall be tested and tuned to ensure the excitation system has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- If it is determined that a change in PSS settings or the addition of a PSS to a synchronous Generation Resource would improve overall system performance, ERCOT shall coordinate with the Generation Resource owner to determine appropriate settings.  Within 180 days of determining appropriate settings, the Generation Resource owner shall revise the PSS setting and/or install the PSS.  Any PSS setting established pursuant to this section shall be established to dampen modes with oscillations as directed by ERCOT and place the PSS in-service.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

- At least every five years, Generation Entities shall conduct performance tests on PSS settings or verify PSS performance based on operational data.  If PSS equipment characteristics are modified, the Generation Entity shall conduct a performance test within 30 days of the modification.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date

- The results of PSS tests or PSS performance verification shall be supplied to ERCOT and the TSP within 30 days of a request from ERCOT.