## Slide 1: PDCWG Report to ROS
February 10, 2011
Sydney Niemeyer

## Slide 2
CPS1 = 145.03

## Slide 6
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 150.90

## Slide 7
CPS 2 92.48

## Slide 9: January Frequency Events
Sunday Jan 9, 2011 @ 18:52
  516 MW -480 MW/0.1 Hz 73% of Bias
Tuesday Jan 11, 2011 @ 06:50
  523 MW -570 MW/0.1 Hz 87% of Bias
Thursday Jan 20, 2011 @ 00:02
  785 MW -397 MW/0.1 Hz 74% of Bias
Friday Jan 21, 2011 @ 03:46
  624 MW -364 MW/0.1 Hz 56% of Bias
Sunday Jan 23, 2011 @ 14:53
  461 MW -310 MW/0.1 Hz 48% of Bias

## Slide 11
Frequency Rate of Change Hz/second
-94.9 micro Hz/second/MW Tripped (less negative number indicates more grid inertia)

## Slide 13
Frequency Rate of Change Hz/second
-84.1 micro Hz/second/MW Tripped (less negative number indicates more grid inertia)

## Slide 15
Frequency Rate of Change Hz/second
-114.6 micro Hz/second/MW Tripped (less negative number indicates more grid inertia)

## Slide 17
Frequency Rate of Change Hz/second
-75.3 micro Hz/second/MW Tripped (less negative number indicates more grid inertia)

## Slide 19
Frequency Rate of Change Hz/second
-100.0 micro Hz/second/MW Tripped (less negative number indicates more grid inertia)

## Slide 20: Event Summary
Lowest inertia event Jan 20, -114 micro Hz/second/MW lost.
Lowest Primary frequency response:
  At Point C for UFLS protection -320 MW/0.1 Hz Jan 20.
  At Point B for sustained response -310 MW/0.1 Hz Jan 23.
Jan 21 and 23 events did not sustain response and had low performance.
Primary Frequency response withdrawal is still apparent on some Resources. Not all Responsive Reserve capacity is frequency responsive. (duct burners, steam augmentation and inlet chillers require equipment to be placed in service.

## Slide 21: Next Meeting
March 2, 2011 ERCOT Met Center