## Slide 1: PDCWG Report on ERCOT Frequency Rate of Change 2010 and January 2011 Frequency Response
ERCOT ROS
February 18, 2011
Sydney Niemeyer & David Kee

## Slide 2: Report Contents
2010 Frequency Event’s Rate of Change in Frequency and Grid Inertia.
  Slide 3 through 78.
January 2011 Frequency Response Performance during five events.
  Slide 79 through 92.

## Slide 3: Highest Rate of Change in Frequency
Using high speed frequency data, the rolling one second change in frequency is calculated.
From the most negative rate of change in frequency (highest change in frequency within any one second period) during the initial frequency decline, the frequency change per MW of imbalance is calculated.
  Hz per second per MW lost.
  Example: -0.067 Hz/second maximum rate of change of frequency during the trip of a 585 MW generator.
    -0.067/585 MW = -0.000115 Hz/second/MW lost. (115 µHz/sec/MW)
    A more negative number between different events indicates lower Grid Inertia.

## Slide 4: Lowest Inertia Events in 2010
Oct 31, 2010 @ 00:11:02 -145 µHz/sec/MW.
Dec 19, 2010 @ 02:39:27 -142 µHz/sec/MW.
Feb 27, 2010 @ 22:55:04 -138 µHz/sec/MW.
Mar 25, 2010 @ 00:11:42 -136 µHz/sec/MW.
Sep 19, 2010 @ 06:59:52 -127 µHz/sec/MW.
Apr 7, 2010 @ 00:33:50 -126 µHz/sec/MW.
Nov 7, 2010 @ 01:57:54 -126 µHz/sec/MW.

## Slide 5
Highest rate of change in any one second period during the frequency decline.
Highest rate of change in any one second period during the frequency reset. Between Point C and Point B.
-115 µHz/sec/MW

## Slide 13: Next set of Slides
Each 2010 event with frequency rate of change. (Slide 13 through 80)
Close up look at Nov 3rd LaaR tripping and frequency rate of change. (Slide 63)
Summary (Slide 77)

## Slide 63
Note: 1445.83 MW actual generation trip. 680 MW of LaaR tripped @ 59.700 Hz plus relay & breaker time beginning before Pt C for a net loss of 765 MW. An additional 100 MW of LaaR tripped between Pt B and recovery to 60.00 Hz.

## Slide 64
Point “A”
10:21:05.732
Nadir
10:21:09.206
3.474 seconds after Point “A”.
LaaR tripping contributed to earlier than normal Nadir.
10:21:06.923
Highest Rate of Change @ +1.191 seconds from Point “A”.

## Slide 78: Conclusions
Some correlation between total wind generation and frequency rate of change.
Strong correlation between total energy and frequency rate of change.
Size of Resources lost as percent of total energy correlates to frequency nadir closer than total wind generation as a percent of total energy.

## Slide 79: Frequency Response Performance to January 2011 Events
Slides 80 through 92

## Slide 80: Two Part Analysis
Calculation of Interconnection Frequency Response at a average Point B settling frequency.
Calculation of frequency rate of change per MW of grid imbalance in µHz/second/MW lost.
Last two events had low frequency response that was not sustained. (Frequency response at Point B was lower than Point C response).

## Slide 81: January Frequency Events Point B Average Frequency Response
Sunday Jan 9, 2011 @ 18:52
  516 MW -480 MW/0.1 Hz 73% of Bias
Tuesday Jan 11, 2011 @ 06:50
  523 MW -570 MW/0.1 Hz 87% of Bias
Thursday Jan 20, 2011 @ 00:02
  785 MW -397 MW/0.1 Hz 61% of Bias
Friday Jan 21, 2011 @ 03:46
  624 MW -364 MW/0.1 Hz 56% of Bias
Sunday Jan 23, 2011 @ 14:53
  461 MW -310 MW/0.1 Hz 48% of Bias

## Slide 82
Frequency Response Sustained!

## Slide 83
Frequency Rate of Change Hz/second
-94.9 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 84
Frequency Response Sustained!

## Slide 85
Frequency Rate of Change Hz/second
-84.1 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 86
Frequency Response Sustained!

## Slide 87
Frequency Rate of Change Hz/second
-114.6 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 88
Frequency Response Withdrawn!

## Slide 89
Frequency Rate of Change Hz/second
-75.3 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 90
Frequency Response Withdrawn!

## Slide 91
Frequency Rate of Change Hz/second
-100.0 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 92: Event Summary
Lowest inertia event Jan 20, -114 µ Hz/second/MW lost.
Lowest Primary frequency response:
  At Point C for UFLS protection -320 MW/0.1 Hz Jan 20.
  At Point B for sustained response -310 MW/0.1 Hz Jan 23.
Jan 21 and 23 events did not sustain response and had low performance.
Primary Frequency response withdrawal is still apparent on some Resources. Not all Responsive Reserve capacity is frequency responsive. (duct burners, steam augmentation and inlet chillers require equipment to be placed in service.)