ERCOT Operations Report

Jan 2011 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 1/4/2011 0:12 | 59.899 | 4 | Out of URS |
| 1/7/2011 6:01 | 59.790 | 388 | Expected Gen Deviation -2200 in 3 mins; out of URS |
| 1/9/2011 3:49 | 59.884 | 32 | Units coming offline with 665 MW due to weather condition and line outages |
| 1/9/2011 18:52 | 59.842 | 76 | Unit trip with 540 MW |
| 1/11/2011 6:50 | 59.871 | 52 | Unit trip with 522 MW |
| 1/14/2011 7:47 | 59.894 | 16 | Unit trip with 465 MW |
| 1/15/2011 7:04 | 59.841 | 248 | Expected Gen Deviation -1250 in 3 mins; out of URS |
| 1/18/2011 6:01 | 60.111 | 11 | Expected Gen Deviation +800 MW in 3 mins due to combined cycle units on TEST mode ramping up fast; out of DRS |
| 1/19/2011 4:58 | 60.102 | 13 | Expected Gen Deviation +800 MW in 2 min; out of DRS |
| 1/19/2011 6:05 | 59.899 | 16 | Expected Gen Deviation -1100 MW in 3 mins; slow URS response |
| 1/20/2011 0:01 | 59.769 | 209 | Unit trip with 890 MW |
| 1/20/2011 7:01 | 59.857 | 224 | Expected Gen Deviation -1200 MW in 2 mins; out of URS |
| 1/21/2011 3:46 | 59.852 | 148 | Unit trip with 650 MW |
| 1/21/2011 10:01 | 59.870 | 172 | Unit trip with 180 MW; out of URS |
| 1/23/2011 14:53 | 59.846 | 160 | Unit trip with 400 MW |
| 1/28/2011 5:21 | 59.875 | 8 | Unit trip with 370 MW |
| 1/29/2011 22:29 | 59.840 | 36 | Unit output reduced by 450 MW due to valve problems |
| 1/30/2011 16:01 | 60.101 | 8 | Expected Gen Deviation +670 MW in 2.5 mins; out of DRS |
| 1/31/2011 0:01 | 59.895 | 12 | Expected Gen Deviation -1200 in 4 mins; out of URS |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 1/23/11 14:56:10 | 1/23/11 15:12:10 | 0:16:00 | 400 |  |

RUC Capacity Purchases

| Details | Unit Days |
| --- | --- |
| Coast | 5 |
| East | 4 |
| Far West | 10 |
| North Central | 9 |
| South | 31 |
| South Central | 25 |
| Grand Total | 84 |

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Aspermont - Spur 138kV | Spur 138/69kV AXFMR1 | 4 |
| Lewisville Switch 345/138kV AT1 | Lewisville Switch - Lewisville Jones Street 138kV | 4 |
| BASE CASE | Syntex - Syntex Tap 69kV | 3 |
| BASE CASE | Victoria - Thomaston 138kV | 3 |
| Singleton - Tomball & Roans Prairie 345kV | Garrott - Midtown 138kV | 3 |
| Singleton - Tomball & Roans Prairie 345kV | Jewett - Rattlesnake Road Switch 345kV | 3 |
| Calaveras - Streich 138kV | West Side - Five Points 138kV | 3 |
| Braunig - Streich 138kV | West Side - Five Points 138kV | 3 |
| BASE CASE | Matador - Paducah 69kV | 2 |
| BASE CASE | Notrees - Notrees Switch 138kV | 2 |
| Fern Street - Ball Park 138kV | West Side - Five Points 138kV | 2 |
| Willow Valley Switch - Lamesa 138kV | Ackerly Vealmoor Sw - Ackerly 69kV | 2 |
| Nueces Bay - Koch Upriver & Lon Hill 138kV | Hiway 9 - Air Liquid AEP 69kV | 2 |
| Parker Switch - Eagle Mountain SES & Roanoke Switch 345kV | Lewisville Switch - Lewisville Jones Street 138kV | 2 |
| Lewisville Switch - Carrolton Northwest 345kV | Lewisville Switch - Lewisville Jones Street 138kV | 2 |
| Air Liquid AEP - Valero East 69 kV | Koch Up River 138_69A1 XFMR | 2 |
| BASE CASE | TH Wharton 138kV/13.2kV Transformer 4A | 1 |
| Singleton - Tomball & Roans Prairie 345kV | Singleton - O'brien 345kV | 1 |
| Singleton - Tomball & Roans Prairie 345kV | Singleton - TH Wharton 345 kV | 1 |
| Singleton - Tomball & Roans Prairie 345kV | Singleton - O'brien 345kV | 1 |
| Lon Hill - Nelson Sharpe 345kV | Nelson Sharpe - Celanese Bishop 138kV | 1 |
| Braunig - Toyota & Valley 138kV | West Side - Five Points 138kV | 1 |
| North Edinburg - Lon Hill 345kV | Rio Hondo 345kV Series Capacitor 1 | 1 |
| Moss Switch - Holt Switch 138kV | Odessa North 138/69kV AXFMR1 | 1 |
| Austrop - Lost Pines 345kV | Austrop 345/138kV AT1 | 1 |
| Farmersville - Monticello SES 345kV | Monticello SES - Sulphur Springs Switch 345kV | 1 |
| Tonkawa Switch - Gibbons Creek & Jack Creek 345kV | Jewet - Singleton 345kV | 1 |
| Tonkawa Switch - Gibbons Creek & Jack Creek 345kV | Jewett - Singleton 345kV | 1 |
| Tonkawa Switch - Gibbons Creek & Jack Creek 345kV | Jewett - Limestone Plant 345kV | 1 |
| Tonkawa Switch - Gibbons Creek & Jack Creek 345kV | Jewett - Singleton 345kV | 1 |
| Ingleside Cogen Switch - Oxychem Corpus Christi 138kV | Dupont PP1 Ingleside - Dupont Switch Ingleside 138kV | 1 |
| Bosque Switch - Whitney 138kV | Bosque Switch - Lake Whitney 138kV | 1 |
| Zorn 345/138kV 23AT1 | Zorn 345/138kV 72AT2 | 1 |
| Lytton Springs 345/138kV AT2 | Lytton Springs 345/138kV AT1 | 1 |
| Garfield - Lytton Springs & Austrop - Zorn 345kV | Austrop 345/138kV AT1 | 1 |
| Base Case | Gold Switch - Brand TU 138kV | 1 |
| DCKT Sandow - Temple Switch 345kV | Hearne 138/69kV AT1 | 1 |
| Oklaunion - Fisher Road 345kV | Liberta REA - Pauline 69kV | 1 |
| Pawnee - Lon Hill 345kV | Sinton - Skidmore 138kV | 1 |
| Santa Anna - Ballinger 138kV | Ballinger - Humble 69kV | 1 |
| Fort Worth - West Denton 138kV | West Denton - Jim Christal Substation 138kV | 1 |
| Graham SES - Breckenridge 138kV | Graham SES - Breckenridge Tap 138kV | 1 |
| Ballinger 138/69kV AT1 | Abilene South - Cedar Gap TEC 69kV | 1 |
| Watermill Switch - Desoto Switch & Cedar Hill Switch 345kV | West Levee Switch 345/138kV AT1 | 1 |
| Parker Switch - Eagle Mountain SES & Roanoke Switch 345kV | Carrollton Northwest - LKPNT 138 kV | 1 |
| Denton - Argyle & West Denton 138kV | West Denton - Jim Christal Substation 138kV | 1 |
| Jewett - Lake Creek SES 138kV | Navarro - Richland 69kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 18 |
| Valley Import | 3 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 01/31/2011 | Nodal Transmission and Security Desk V1 Rev4 | 521 |
| 01/31/2011 | Nodal Resource Desk V1 Rev3 | 520 |
| 01/31/2011 | Nodal Reliability Unit Commitment V1 Rev3 | 519 |
| 01/31/2011 | Nodal Real Time Desk V1 Rev4 | 518 |
| 01/31/2011 | Nodal DC Tie Desk V1 Rev2 | 517 |
| 01/31/2011 | Nodal Shift Supervisor Desk V1 Rev2 | 516 |
| 01/05/2011 | Nodal Transmission and Security Desk V1 Rev3 | 515 |
| 01/05/2011 | Nodal Real Time Desk V1 Rev3 | 514 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

01/15 01:00   	ERCOT issued an Emergency Notice for the loss of EMS.

01/15 07:15	ERCOT issued an Emergency Notice for the loss of RLC.

01/15 07:17	ERCOT issued an Emergency Notice for the loss of EMS.

Communication Issues

None

## ERCOT peak (Unofficial)

01/21 08:00 50,715 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2008 | 2009 | 2010 | 2011 |
| January | 3.30 | 4.11 | 3.78 | 2.91 |
| February | 3.59 | 3.49 | 3.79 | NA |
| March | 3.29 | 3.24 | 2.24 | NA |
| April | 2.45 | 2.66 | 2.47 | NA |
| May | 3.01 | 2.90 | 2.63 | NA |
| June | 2.81 | 2.89 | 2.84 | NA |
| July | 2.55 | 2.83 | 2.39 | NA |
| August | 3.66 | 3.07 | 2.29 | NA |
| September | 4.99 | 3.68 | 3.14 | NA |
| October | 2.79 | 2.92 | 2.37 | NA |
| November | 2.60 | 1.93 | 3.46 | NA |
| December | 4.54 | 3.70 | 2.60 | NA |
| Annual Average | 3.29 | 3.11 | 2.83 | 2.91 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 1/1/2011 | 20:05 | Advisory issued to all QSE PRC below 3000 MW. |
| 1/2/2011 | 8:11 | ERCOT is issuing an Advisory due to PRC being below 3000 MW. Real Time Desk Operator made hotline call. |
| 1/2/2011 | 6:44 | ERCOT issued an OCN for Projected Reserve Capacity Shortage for HE 10-12. |
| 1/4/2011 | 7:11 | ERCOT issued advisory for PRC below 3000 MW. |
| 1/4/2011 | 9:43 | ERCOT issued Advisory for PRC below 3000 MW. |
| 1/4/2011 | 7:10 | ERCOT issued an Advisory due to PRC has fallen below 3000 MW. |
| 1/4/2011 | 9:43 | ERCOT issued an Advisory due to PRC has fallen below 3000 MW. |
| 1/5/2011 | 7:11 | ERCOT issued advisory for PRC below 3000 MW. |
| 1/5/2011 | 10:08 | ERCOT issued an Advisory due to PRC being below 3000 MW. |
| 1/5/2011 | 2:08 | ERCOT issued an OCN for Projected Reserve Capacity Shortage for HE 19-21. |
| 1/5/2011 | 7:12 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/5/2011 | 10:08 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/5/2011 | 18:03 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/6/2011 | 4:07 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/7/2011 | 6:38 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/15/2011 | 22:13 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/15/2011 | 9:05 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/16/2011 | 10:20 | ERCOT issued an advisory for PRC below 3000 MW. |
| 1/17/2011 | 10:27 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/17/2011 | 10:28 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/20/2011 | 19:20 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/21/2011 | 22:45 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/21/2011 | 22:45 | ERCOT issued an OCN for projected reserve capacity shortage for H.E. 0100, 0200 and 0300 tomorrow. |
| 1/22/2011 | 2:55 | ERCOT is extending the OCN for projected reserve capacity shortage for H.E. 0400 through 1200. |
| 1/23/2011 | 18:30 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/23/2011 | 13:24 | ERCOT issued an OCN for Projected Reserve Capacity Shortfall for hours 19-22. |
| 1/23/2011 | 18:31 | ERCOT issued an Advisory for PRC has fallen below 3000 MW. |
| 1/29/2011 | 9:26 | ERCOT issued an Advisory for PRC below 3000 MW. |
| 1/29/2011 | 9:26 | ERCOT issued an Advisory for PRC has fallen below 3000 MW. |
| 1/30/2011 | 11:22 | ERCOT issued an Advisory for PRC being below 3000 MW. |
| 1/30/2011 | 8:51 | ERCOT issued an OCN for projected reserve capacity shortage for H.E. 1200 through 1500. |
| 1/30/2011 | 11:23 | ERCOT issued an Advisory for PRC has fallen below 3000 MW. |
| 1/31/2011 | 18:16 | ERCOT issued an OCN for Projected Reserve Capacity shortage HE11-HE22 on 2-1-11. |

Transmission Watch

None

Emergency Notice

01/15 01:00   	ERCOT issued an Emergency notice for the loss of EMS.

01/15 07:15	ERCOT issued an Emergency notice for the loss of RLC.

01/15 07:17	ERCOT issued an Emergency notice for the loss of EMS.

Texas RE Event Analysis

01/09 03:38	Simultaneous loss of three 345kV lines, two 138kV lines, one 69kV line, one 345/138kV Autotransformer, one 138/69kV Autotransformer, one 138kV Bus and loss of multiple units for a total of 654 MW of generation in the Corpus Christi area. Effects of severe storm being experienced in the area at the time.

Others

None