| NPRR Number | 282 | NPRR Title | Dynamic Ramp Rates Use in SCED |  |
| --- | --- | --- | --- | --- |
| Timeline | N/A | Action |  | Recommended Approval of Impact Assessment |
| Date of Decision |  | February 17, 2011 |  |  |
| Effective Date |  | Upon System Implementation. |  |  |
| Priority and Rank Assigned |  | Priority Critical |  |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 6.5.7.1.12, Resource Limits 6.5.7.2, Resource Limit Calculator |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) proposes revisions that are intended to result in more reasonable Dispatch of Generation Resources when a telemetered Base Point requires the Resource to employ technologies that in turn change the Resource’s ramp rate. For example, when Security-Constrained Economic Dispatch (SCED) generates a new Base Point for a unit that is currently at baseload, SCED uses a static ramp rate found in the Resource Parameters database that does not accurately reflect the dynamic ramp rate that the unit can deliver as it leaves baseload status (ten MW/min. for some units) and goes into duct burners (one MW/min. for some units) or through duct burners into other technologies such as certain forms of power augmentation. Instead of using the declared static ramp rates at designated output levels, SCED should use a dynamic ramp rate that can be telemetered by the Qualified Scheduling Entity (QSE) to ERCOT using the Inter-Control Center Communications Protocol (ICCP) database with an update rate of two or four seconds, which will better match the unit’s ramp rate capability during the SCED execution. The up and down ranges of this telemetered dynamic ramp rate are best defined by ERCOT based on its experience in the Nodal Market trials and its view of the SCED Base Point outcomes and its analysis of the Generation Resource Energy Deployment Performance (GREDP) scores and Regulation Service deployed. |  |  |
| Reason for Revision |  | Market trials demonstrate that plants are Dispatched at levels that are unachievable during the five-minute SCED intervals. These situations occur when SCED uses a declared static ramp rate for an output level that does not apply over the output range implicated by the new telemetered Base Point. |  |  |
| Procedural History |  | - On 1/18/11, the ERCOT Board considered NPRR282. - On 2/10/11, a revised Impact Analysis and Cost Benefit Analysis were posted. - On 2/17/11, PRS considered the impact assessment for NPRR282. |  |  |
| PRS Decision |  | On 2/17/11, PRS unanimously voted to endorse and forward the impact assessment for NPRR282 to TAC. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 2/17/11, ERCOT Staff sought PRS endorsement of impact assessments for “Phase 1” parking deck NPRRs. It was emphasized that language had already been approved by the ERCOT Board for NPRR282. |  |  |
| Board Decision |  | On 1/18/11, the ERCOT Board approved NPRR282 as recommended by TAC in the 12/6/10 TAC Report. |  |  |

| Sponsor |  |
| --- | --- |
| Name | Randy Jones |
| E-mail Address | rajones@calpine.com |
| Company | Calpine |
| Phone Number | 713.830.8846 |
| Cell Number | 832.385.3322 |
| Market Segment | Independent Generator |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Ann Boren |
| E-Mail Address | aboren@ercot.com |
| Phone Number | 512-275-7411 |