| NOGRR Number | 052 | NOGRR Title | Conductor/Transformer Transmission Facility Rating |
| --- | --- | --- | --- |

| Date | March 1, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | David Bogen |
| E-mail Address | dbogen@oncor.com |
| Company | Oncor Electric Delivery |
| Phone Number | (214) 743-6735 |
| Cell Number |  |
| Market Segment | Investor Owned Utility |

Comments

In determining the 15 -Minute Rating, this Nodal Operating Guide Revision Request (NOGRR) requires that only a 90% pre-load be used for this calculation. The Transmission Service Provider (TSP) Rating Methodology document that Oncor has filed with ERCOT specifies that Oncor uses an 84% pre-load for this calculation. For a more detailed explanation of the Oncor’s rating methodology, see https://mis.ercot.com/pps/tibco/mis/Pages/Grid+Information/Long+Term+Planning. (Look under Network Operations Model/TSP Rating Methodology.) Oncor made this determination based on historical statistical analysis of the loading of Oncor’s transmission system. Oncor would like to see this Nodal Protocol Revision Request (NPRR) be modified such that it will allow for a preloading of up to 90% so the TSPs can develop ratings more appropriate for their transmission system to provide better utilization of the transmission system.

If this modification is not made Oncor will be required to resubmit ratings for all transmission lines and autotransformers. The resubmitted 15-Minute Ratings would be lower than the current information that has been submitted to ERCOT.

This change will also align the NOGRR with the comments submitted by Oncor on NPRR324.

Revised Proposed Guide Language

- 3.7.4	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the rating of their facilities and shall send the methodology used to ERCOT  in accordance with paragraph (3) of Protocol Section 3.10, Network Operations Modeling and Telemetry.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide ERCOT with four nominal Transmission Element Ratings:

(a)	Normal Rating:  Represents the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

(b)	Emergency Rating:  Represents the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure.

(c)	15-Minute Rating:  Represents the 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading up to 90% of the Normal Rating.  The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading up to 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

(d)	Conductor/Transformer Rating:  Represents the two hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The conductor or transformer can operate at this rating for two hours without violation of National Electrical Safety Code (NESC) clearances or equipment failure.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Element to within Normal Ratings as soon as practicable, based on Good Utility Practice.