| OGRR Number |  | OGRR Title |  |
| --- | --- | --- | --- |
| Date Posted |  |

| Operating Guides (OG) Section(s) Requiring Revision (Include Section No. and Title) | 2.7.1 Introduction 2.7.4.1 maintaining System Voltage |
| --- | --- |
| Protocol Section(s) Requiring Revision, if any |  |
| Requested Resolution (Normal or Urgent, and justification for Urgent status) |  |
| Revision Description |  |
| Reason for Revision |  |
| Overall Market Benefit |  |
| Overall Market Impact |  |
| Consumer Impact |  |

Quantitative Impacts and Benefits

Instructions:  To allow for comprehensive OGRR consideration and development of the Cost Benefit Analysis (CBA), please fill out each block below completely and provide as much detailed information as possible.  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to this OGRR.

| Assumptions | 1 | e.g.: Key assumptions used in estimating market cost and/or benefit |
| --- | --- | --- |
|  | 2 | Dependencies on other projects or other timing requirements |
|  | 3 |  |
|  | 4 |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | e.g.: Cost per MP to implement | e.g.: $10,000 each for 50 QSEs |
|  | 2 | Add’l staff required per MP | 1.5 FTE each for 6 TDSPs @ $65/hour |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | e.g.: Reduced MP costs | e.g.: 2 FTE reduction for 25 CRs @ $65/hour |
|  | 2 | Enhanced MP efficiency | 2 hour savings per day for 50 generators @$65 |
|  | 3 | Reduced congestion cost | 0.5% reduction in total congestion cost |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | e.g.: Benefits that are difficult to quantify |
|  | 2 | Benefits that are not certain but relatively likely |
|  | 3 | Customer service impacts, cash flow impacts, transaction speed, etc. |
|  | 4 |  |
| Other Comments | 1 | e.g.: Thoughts on ERCOT systems impacts |
|  | 2 | Potential manual workarounds or delivery options |
|  | 3 | Other comments of value to PRS, TAC and the Board of Directors |
|  | 4 |  |

| Sponsor |
| --- |
| Name |  |
| E-mail Address |  |
| Company |  |
| Phone Number |  |
| Cell Number |  |
| Market Segment |  |

| Market Rules Staff Contact |
| --- |
| Name |  |
| E-Mail Address |  |
| Phone Number |  |

Proposed Guide Language Revision

Instructions:  Guidelines and helpful hints may be found at the following link: http://www.ercot.com/mktrules/protocols/index.html.

Please remember the following:

- Use the most current version of the Guide language, which is available on the ERCOT website.

- Show original Guide baseline language in black.

- Present the entire titled (sub) section as the baseline – not just the paragraphs subject to revision.

- Make all revisions in redlined format (using “Track Changes”).  Be sure to change the user name to the appropriate individual or company name.  Do NOT show revisions by changing font color or font strikethrough.

- Use highlighting when inserting non-Guide language comments (like questions) into Guide language.

- Be sure proposed changes are reflected in both boxed and unboxed sections, if appropriate.

Insert proposed Guide language here.

2.7	System Voltage Profile

2.7.1	Introduction

(1)	The system Voltage Profile is a predetermined desired nominal voltage set point at the high voltage side of generator busses to maintain transmission voltages  across the ERCOT Region.

(2)	ERCOT shall coordinate and conduct studies with the Transmission Service Providers (TSPs) to determine the normally desired Voltage Profile for all Generation Resource busses in the ERCOT Region as specified in item (1), Protocol Section 3.15, Voltage Support as published on the ERCOT Market Information System (MIS) Secure Area.

(3)	ERCOT shall establish and update Voltage Profiles at points of interconnection of Generation Resources. The Voltage Profile at the point of interconnection of Generation Resource will be  maintained within the capabilities of the Generation Resource as specified in 3.15 (4) of the ERCOT Protocols and in conjunction with other dynamic and static devices on the ERCOT Transmission Grid.

2.7.2	Maintaining Voltage Profile

ERCOT has the responsibility for monitoring and controlling the Voltage Profile and should use the following:

(a)	Operations Engineering

(i)	All voltage limits must be based on sound engineering studies that use the appropriate Network Operations Model.  TSP study results should be made available to ERCOT; and

(ii)	Transfer limits shall reflect voltage and/or reactive restrictions.

(b)	Coordination

(i)	Entities must coordinate high voltage limits in order to guarantee that the maximum continuous over-voltage of equipment is not exceeded.  Transmission Operators (TO) shall notify ERCOT of normal operating voltage limits and post-contingency voltage limits for each bus;

(ii)	Low voltage limits must be coordinated in order to prevent one Entity from being a burden to another;

(iii)	Voltage limits shall not be violated during all normal and first contingency conditions; and

(iv)	The operation of all Reactive Power devices under the control of a TO or a Qualified Scheduling Entity (QSE) will be coordinated under the direction of ERCOT to maintain transmission voltage levels within normal limits and post-contingency voltages within post contingency limits.  Static reactive devices will be managed to ensure that adequate dynamic reactive reserves are maintained at all times.

(c)	Notification

(i)	Generation Resources with voltage problems shall notify the TO to whom they are directly connected.  TOs shall notify other affected TOs and ERCOT; and

(ii)	ERCOT will monitor events and may direct actions to solve the problem.

(d)	Response

(i)	When the voltage levels deviate from established limits, ERCOT or the delegated TO shall take immediate steps to relieve the condition using all available reactive resources.

(e)	Monitoring

(i)	TOs shall provide telemetry to ERCOT on all major transmission bus voltages.

(f)	Controls

(i)	ERCOT must be aware of the locations of available reactive capability;

(ii)	ERCOT shall maintain displays to monitor Voltage Profiles and reactive flows; and

(iii)	Controls to maintain Voltage Profiles may include but are not limited to Capacitor switching, reactor switching, auto-transformer tap changing, generator reactive dispatch, transmission line switching, and Load shedding.

(g)	Documentation

(i)	Each TO must maintain a voltage/reactive plan for normal and Emergency Conditions and will provide this plan to adjacent TOs as well as ERCOT upon request.

(h)	Emergency or Abnormal Conditions

(i)	Transmission systems shall be designed so that effective reactive reserves shall be available without de-energizing other Facilities or shedding Load under normal conditions;

(ii)	Major transmission lines shall be kept in service during light Load as much as possible.  Lines should only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded; and

(iii)	Voltage reduction should not be done on the transmission system unless coordinated with adjacent TOs.

2.7.3	Special Consideration for Nuclear Power Plants

In all planning studies and Real-Time operations, ERCOT and TOs shall maintain the switchyard voltage at each nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission.  ERCOT shall notify the QSE representing a nuclear power plant of the result of any studies where the voltage at the plant switchyard cannot be adequately maintained.  ERCOT and the TO shall monitor the voltage in Real-Time and provide notice to the QSE representing the nuclear power plant of any voltage inadequacy at the plant switchyard that cannot be corrected within 30 minutes.  High and low limits on switchyard voltage at each nuclear power plant necessary to meet these requirements shall be specified in ERCOT Procedures.

2.7.4	Reactive Considerations for Generation Resources

2.7.4.1	 Maintaining System Voltage

(1)	ERCOT will maintain a performance log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests.  QSEs responding in less than two minutes from the time of issuance of such requests shall be deemed satisfactory.

(2)	ERCOT shall monitor the Automatic Voltage Regulator (AVR), as required in Protocol Section 6.5.5.1, Changes in Resource Status, to assure that it is on and operating automatically at least 98% of the time in which the QSE is providing the Reactive Power supply from Generation Resources required to provide Voltage Support Service (VSS).  The percentage is calculated as:  Time (AVR is on while providing Service) / (Total Time Providing Services) (100%).

(3)	Except under Force Majeure conditions or ERCOT-permitted operation of the generating unit, failure of a Generation Resource required to provide VSS to provide either leading or lagging reactive up to the required capability of the unit upon request from a TO or ERCOT may, at the discretion of ERCOT, be reported to the Texas Regional Entity.

(4)	Except under Force Majeure conditions or ERCOT-permitted operation of the generating unit, if a Generation Resource required to provide VSS fails to maintain transmission system voltage at the point of interconnection with the TSP within 2% of the Voltage Profile while operating at less than the maximum reactive capability of the generating unit, ERCOT may, at its discretion, report this to the Texas Regional Entity. If a Generation Resource has a specified Voltage Profile at which the +/- 2% voltage criterion above would meet or exceed the transmission equipment rating or the system low voltage criterion, the Generation Resource will not exceed that transmission limit. These limits will be specified by the TSP at the point of interconnection with the approval of ERCOT.

(5)	The Generation Resource shall make every effort to maintain the most current Voltage Profile as close as possible to the actual desired value at its point of interconnection. The actual desired voltage shall be the voltage most recently published by ERCOT or adjusted by the TSP at the point of interconnection.

(6)	The Texas Regional Entity will investigate claims of alleged non-compliance and Force Majeure conditions, and address confirmed non-compliance situations.  The Texas Regional Entity will advise the Generation Resource, its QSE, ERCOT, and the TSP planning and operating staffs of the results of such investigations.

9.3.9	Voltage and Reactive Control Performance Monitoring

[Placeholder]

[NOGRR025: Replace Section 9.3.9, Voltage and Reactive Control Performance Monitoring, above, with the following upon system implementation:] 9.3.9 Voltage and Reactive Control Performance Monitoring (1) ERCOT in coordination with the TSPs shall conduct studies to determine the nominal voltage set points across the ERCOT System for all Electrical Buses used for voltage support and shall post all Voltage Profiles annually on the MIS Secure Area. (2) Transmission owners shall provide switching plans for automatically controlled reactors, capacitors, and other reactive controlled sources to ERCOT. For manually switched reactive devices, the transmission owner shall provide its guidelines for the operation of these devices. These plans and guidelines shall be posted annually to the MIS Secure Area and must be provided in accordance with the NOMCR or other prescribed process.