## Slide 1: Valley Import Constraint
Resmi Surendran

## Slide 2: Valley Import Constraint
Range of SFs
  -0.95 to -0.97 in valley area
  0.03 to 0.045 outside valley area
Not a competitive constraint and hence the Resources are moved based on offers capped by higher of Reference LMP & Mitigated Offer Cap curve
Base case constraint and hence has a default Max Shadow Price of $5000/MWh

## Slide 3: Issue
Highest Shadow Price when not violated is less than $100/MWh (more than 28hrs after go live)
  Constraint cannot be resolved many times even with all the generation available
South LZ SPP when the constraint is violated ranges from $1500/MWh to $1850/MWh (roughly 15 hrs after go live)
  Demand response in majority of that load zone with the high price have no impact to the constraint.
Constraint is manually handled after it has been violated for more than an hour in SCED (roughly 65 hrs after go live)

## Slide 4: Potential Long Term Solution
Develop transmission network to support load growth.
Create a Load Zone for Valley to encourage demand participation that has impact on the constraint

## Slide 5: Short Term Solution
Reduce Max Shadow Price and let the constraint be managed by SCED and provide price signal to encourage new generation development or load participation
  Import from DC tie is limited during peak hours
  Demand participation would be less since the deployment would be for long hours and payments would be based on the South LZ SPP
Revalidate the limit calculations in planning and operations

## Slide 6: Proposed Max Shadow Price - $350/MWh
Should be able to move existing or new Resources to resolve constraint with out manual action
To fully dispatch the highest capped and bounded offer during non-scarcity intervals
The highest offer from a new resource with no verifiable cost that needs to be moved is
  14.5 * high FIP/ lowest SF = 14.5 *10 /0.95 ~ 150
The highest offer from a new resource with verifiable cost that needs be moved is
  (high Heat Rate * High FIP + corresponding high O&M) * highest multiplier/ lowest SF
  (14 .5*10 + 75 )*1.5/0.95 ~ $350/MWh