| NOGRR Number | 067 | NOGRR Title | Review and Analysis of Turbine Speed Governor Performance |
| --- | --- | --- | --- |

| Date | March 21, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Henry Durrwachter |
| E-mail Address | hdurrwachter@luminant.com |
| Company | Luminant Energy Company LLC |
| Phone Number | 214-875-9285 |
| Cell Number | 214-437-4622 |
| Market Segment | Investor-Owned Utility (IOU) |

Comments

Upon further review of the changes proposed in NOGRR067, Review and Analysis of Turbine Speed Governor Performance, Luminant Energy Company LLC (Luminant) believes that it is more efficient and more appropriate for the Resource Entity and not the Qualified Scheduling Entity (QSE) to submit turbine governor speed tests to ERCOT and to review and analyze Generation Resource performance during frequency events.

The Resource Entity is clearly more closely acquainted with the design and operational characteristics of their Resource than is the QSE, who may be an unaffiliated third-party.  And since it is the Resource Entity that actually conducts the testing of the turbine governor, why should the QSE be required to submit the test report?  That just adds an unnecessary step into the process.  Therefore, our changes below require the Resource Entity to supply turbine speed governor test results to ERCOT and to be the party that reviews Generation Resource performance during frequency events.

Revised Proposed Guide Language

2.2.7	Turbine Speed Governors

(1)	A Governor shall be in-service whenever the Generation Resource is providing energy to the ERCOT Transmission Grid.

(2)	Resource Entities shall conduct Governor performance tests for each Generation Resource or Wind-powered Generation Resource (WGR) at least every two years using one of the test methods or historical methods specified in Section 8, Attachment C, Turbine Governor Speed Tests.  The Resource Entity shall then provide test results to ERCOT.

(3)	Every effort should be made to maintain Primary Frequency Response. Maintenance  Tests on Governors shall demonstrate calibration for operation consistent with a generator droop characteristic of no greater than 5% but no less than 2% and Governor Dead-Band no greater than +/- 0.036 Hz.

(4)	There are elements that can contribute to poor Primary Frequency Response.  These include:

(a)	Governor Dead-Band in excess of +/- 0.036 Hz (measured from 60 Hz);

(b)	Valve position limits;

(c)	Blocked Governor operation;

(d)	Control mode;

(e)	Adjustable rates or limits;

(f)	Boiler/turbine coordinated control or set point control action; and

(g)	Automated “reset” or similar control action of the turbine’s MW set point.

(5)	Every attempt should be made to minimize the effects of the elements listed in item (4) above on the Governor operation for the duration of all frequency disturbance events.  Each Resource Entity should review and analyze the performance of its Generation Resources during frequency disturbance events to verify that these elements do not contribute to a Governor droop characteristic of no greater than 5% but no less than 2%.

(6)	If ERCOT determines that ERCOT System reliability would be enhanced, for a defined period of time, ERCOT may direct WGRs under the control of a Special Protection System (SPS) to limit power increases due to frequency if there is risk of an SPS operation due to a low frequency event.