## ERCOT alerts_notices
# | Source | ID | Type + Report | Priority | Summary | Description | Audience | # of Txns 01/2011 | MISUG Comments
1 | EMS | BCABRANCH | Telemetry | High | ALERT: <SUBSTATION : EQUIPMENT IDENTIFICATION> <value> TEL OVERLOAD | Once transmission line and transformer Dynamic Ratings are retrieved, ERCOT shall compare the actual flow and state estimated flow calculation of MVA to the effective Transmission Element limit and, if an out-of-limit condition exists, ERCOT shall produce an overload notification | A TSP | 0
2 | EMS | BCABRANCH | Telemetry | High | ALERT: <SUBSTATION : EQUIPMENT IDENTIFICATION> <value> SE OVERLOAD | Once transmission line and transformer Dynamic Ratings are retrieved, ERCOT shall compare the actual flow and state estimated flow calculation of MVA to the effective Transmission Element limit and, if an out-of-limit condition exists, ERCOT shall produce an overload notification | A TSP | 0
3 | EMS | BCRSMTCH | Telemetry | High | ALERT :<RES_ID> - TEL MW= <VALUE> TRANS SUM= <VALUE> | Add a SCADA calculation to sum the Mw telemetry of transmission lines moving power from a generating plant. Compare this total to the sum of the telemetered Mw output of the Resources at the same plant. Alarm the QSE if the amount exceeds a threshold. | A QSE | 0
4 | EMS | BCVOLLUN | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],SE SGU ERROR MW=[123] TSUM=[1234], | ERCOT shall notify each QSE representing the Split Generation Resource of any errors in telemetry detected by the State Estimator. | A QSE | 0
6 | EMS | LFUPDT | Market Message | High | ERCOT 7 DAY LF UPDATED <Add Alert Time> | ERCOT System, Weather Zone, and Load Zone Load forecasts for the next seven days, by hour, and a message on update indicating any changes to the forecasts by means of the Messaging System; | All MPs | 16614
7 | EMS | RLCCCNO | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: INVALID CC CONFIG | For Combined Cycle configuration number validation, set it to default or last good value not 0. * | A QSE | 1296
8 | EMS | RLCHCAP | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],HSL > THAN CURCAP | HSL is higher than the net dependable capability | QSE | 0
9 | EMS | RLCHLSL | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: INVALID TEL HSL OR LSL | Invalid HSL or LSL telemetry (quality suspect). * | A QSE | 26389 | possible to have an RST check (ex. When HSL is 0)?
10 | EMS | RLCHSLAS | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: HSL MINUS LSL BELOW SUM OF AS RESP | HSL - LSL < Sum of Reg-Up Responsibility, Reg-Down Responsibility, Responsive Responsibility and Non-Spin Responsibility. * | A QSE | 103160 | Looking to remove under the condition of no AS.
11 | EMS | RLCRSTMW | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: INCONSIST RST AND MW | If Resource Status is OFF, and Resource output Mw is greater than 2 Mw, then alarm incorrect status. | A QSE | 144835
12 | EMS | RLCSCEDR | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: SDRAMP BELOW 0 | SCED Down Ramp Rate <= 0. | A QSE | 4072
13 | EMS | RLCSCEUR | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: SURAMP BELOW 0 | SCED Up Ramp Rate <= 0. | A QSE | 2863
14 | EMS | RLCSUSMW | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: SUSPECT TEL HDL=LDL=MW | If the HDL = LDL = Actual Generation and Resource Status is not OFF then alarm the QSE operator to verify data telemetry used by RLC. * | A QSE | 366225 | This Alert should not be issued for units which are OUT or OFF
15 | EMS | RLCUHSL | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: TEL HSL BELOW 0 | The telemetered HSL <= 0. * | A QSE | 48794
16 | EMS | RLCULSL | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: TEL LSL BELOW 0 | The telemetered LSL < 0. * | A QSE | 1
17 | EMS | RLCXGTBD | Telemetry | High | QSE: <QSE_ID> UNIT: <ID> ALERT: INVALID TEL RST | Invalid or suspect resource status codes. * | A QSE | 2
18 | EMS | UNSRSRSS | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],NSPIN AS SCHED < 0 | The Ancillary Schedules (Responsive and Non-Spin) < 0. RLC will set the AS responsibility to 0. | A QSE | 0
19 | EMS | UNSRSRST | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],NSPIN AS RESP < 0 | The Ancillary Responsibilities (Reg-Up, Reg-Down, Responsive and Non-Spin) < 0. RLC will set the AS responsibility to 0. |  | 0
20 | EMS | UREGDN | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],REGDOWN PF < 0 | The Reg-Up/Reg-Down Participation Factors < 0. RLC will set the Reg-Up/Reg-Down Participation Factors to 0. | QSE | 0
21 | EMS | UREGUP | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],REGUP PF < 0 | The Reg-Up/Reg-Down Participation Factors < 0. RLC will set the Reg-Up/Reg-Down Participation Factors to 0. | QSE | 0
22 | EMS | URGDASRT | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],REGDWN AS RESP < 0 | The Ancillary Responsibilities (Reg-Up, Reg-Down, Responsive and Non-Spin) < 0. RLC will set the AS responsibility to 0. |  | 0
23 | EMS | URGUASRT | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],REGUP AS RESP < 0 | The Ancillary Responsibilities (Reg-Up, Reg-Down, Responsive and Non-Spin) < 0. RLC will set the AS responsibility to 0. | A QSE | 0
24 | EMS | URRASRS | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],RESP AS SCHED < 0 | The Ancillary Schedules (Responsive and Non-Spin) < 0. RLC will set the AS responsibility to 0. | A QSE | 0
25 | EMS | URRASRT | Telemetry | High | QSE:[qse], SUBSTATION:[substn], UNIT:[unitname],RESP AS RESP < 0 | The Ancillary Responsibilities (Reg-Up, Reg-Down, Responsive and Non-Spin) < 0. RLC will set the AS responsibility to 0. |  | 0
26 | MMS | CM-ADJCLOSE-NOTF | Market Message | Low | Adjustment window has closed for <MM/DD/YYYY> hr <HH>. | Notify QSEs that the adjustment window has closed | All QSEs | 156560 | Turn off alert.
27 | MMS | CM-ADJOPEN-NOTF | Market Message | Low | Adjustment window has opened for <MM/DD/YYYY>. | Notify QSEs that the adjustment window has opened | All QSEs | 6270 | Turn off alert.
28 | MMS | CM-ASCK-FAIL | COP Warning | High | AS Responsibility Check failed for Trade Date: <MM/DD/YYYY>, Delivery Hour: <HH> for AS Type: <AS_TYPE>. The Total COP is <XX> MW and the AS Difference = <XX> MW | ERCOT shall notify the QSE if the sum of the Ancillary Service capacity designated in the COP for each hour, by service type) is less than the QSE's Ancillary Service Supply Responsibility for each service type for that hour. If the QSE does not correct the deficiency within one hour after receiving the notice from ERCOT, then ERCOT shall follow the procedures outlined in Section 6.4.8.1, Evaluation, and Maintenance of Ancillary Service Capacity Sufficiency. | A QSE | 6946
29 | MMS | CM-ASM-NOTF | Market Message | High | <AS_TYPE>: <AS_TYPE>, RES_NAME:<RESOURCE_NAME>, DEPLOY_MW: <XX.XX>, BEGIN_TIME: <MM/DD/YYYY> <HH>24:MI:SS CST, END_TIME: <MM/DD/YYYY> <HH>24:MI:SS CST, DURATION: <XX.X> Hrs | Notify QSE of AS deployment | A QSE | 290 | Determine how to move to another queue, so it isn't caught up in the other msgs in the queue. Request to create a separate type of message (similar to a RUC instruction). Less than 10 minutes to react to this notice.
30 | MMS | CM-ASTRD-NOTF | Reported Trade | High | AS <AS_TYPE> Trade <Submission/Cancel> update by <PARTICIPANT_NAME>: Confirmed: <NO/YES>, for Trade Date: <MM/DD/YYYY>, Buyer:<PARTICIPANT_NAME>,Seller:<PARTICPANT_NAME> | When an Ancillary Service Trade is reported to ERCOT, ERCOT shall notify the counterparty to the trade. | counterparty to the trade. | 17086 | Collapse identical messages similar to Energy Trades. Only send for confirmed, not for unmatched trades. Timestamp on this msg is used to determine when the CP confirmed the trade.
31 | MMS | CM-ASUND-FAIL-NOTF | Submission Warning | Med | AS Undeliverable for: <raic_resource_name> on trade date: <tradedate> at delivery time <delivery_hour, <HH>24>:<delivery_min> for AS Type: <as_type>, RUC Type: <ruc_type>, Violated MW: <violated_mw> [of <cop_as_mw>]. | Notify QSE | A QSE | 425
32 | MMS | CM-CAPTRD-NOTF | Reported Trade | High | Capacity Trade <Submission/Cancel> update by <PARTICIPANT_NAME>: Confirmed: <NO/YES>, for Trade Date: <MM/DD/YYYY>, Buyer:<PARTICIPANT_NAME, Seller:<PARTICIPANT_NAME> | When a Capacity Trade is reported to ERCOT, ERCOT shall notify the counterparty to the trade. | counterparty to the trade. | 27163 | Collapse identical messages similar to Energy Trades. Only send for confirmed, not for unmatched trades. Timestamp on this msg is used to determine when the CP confirmed the trade.
33 | MMS | CM-CONSCK-FAIL | COP Warning | Medium | Consistency Check for Resource Status failed for Resource:<Resource>, Operating Date: <MM/DD/YYYY> , Operating Hour: <HR>, Cop Status: <Status>, Telemetered Status: <Status> |  | A QSE | 12770 | Good part: COP in RT doesn't match. Bad part: When transitioning from ON to ONREG, during the hour of ON and this runs 5 minutes prior to the top of the next hour, the transition to ONREG hasn't taken place creating this notification. Should this be moved to run after the top of the hour to eliminate the noise of the transitions?
34 | MMS | CM-COPCK-NOTF | COP Warning | Med | Cop Update Check failed for Resource: <RESOURCE_NAME>, Operating Date: <MM/DD/YYYY> , Operating Hour: <HH>, Cop Status: <XX> | Notify QSEs who do not have complete COPs for all hours of the current operating day and the following day | A QSE | 8081
35 | MMS | CM-COPVAL-NOTF | Market Message | High | For CC Unit: UNIT_NAME, there are two or more modes online for Date: <MM/DD/YYYY> | MMS hourly process that checks the COP for combined cycle configurations and will issue warning messages sent to the QSE if two or more configurations are marked as online in any one of the remaining hours of today and all the hours for tomorrow. | A QSEs | 1488
36 | MMS | CM-COPVAL-NOTF | Market Message | High | For resource: <RESOURCE_NAME> the COP Status does not match with the other jointly owned units belonging to Physical <RESOURCE_NAME> for Date: <MM/DD/YYYY> for one or more hours | MMS hourly process that issues warning messages to QSEs if two or more jointly owned units belonging to the same physical resource do not have the same Resource Status in the COP for any of the remaining hours of today and all the hours of tomorrow. | A QSE
37 | MMS | CM-ENGTRD-NOTF | Reported Trade | High | Energy Trade <Submission/Cancel> update by <PARTICIPANT_NAME>: Confirmed: <NO/YES>, for Trade Date: <MM/DD/YYYY>, Buyer:<PARTICIPANT_NAME, Seller:<PARTICIPANT_NAME>, Settlement Point: <SETTLEMENT_POINT> | When an Energy Trade is reported to ERCOT, ERCOT shall notify the counterparty to the trade. | counterparty to the trade. | 132533 | Collapse identical messages similar to Energy Trades. Only send for confirmed, not for unmatched trades. Timestamp on this msg is used to determine when the CP confirmed the trade.
38 | MMS | CM-MKTOPEN-NOTF | Market Message | Low | Market has opened for <MM/DD/YYYY>. | Notify QSEs that the Market has opened | All QSEs | 6270
39 | MMS | CM-OPHRCLOSE-NOTF | Market Message | Low | Market has closed for <MM/DD/YYYY> hr <HH>. | Notify QSEs that the Market has closed | All QSEs | 157320 | Recommend turning this notification off.
40 | MMS | CM-SWCAP-NOTF | Market Message | High | SWCAP has been changed for AS/ENGY to <XXXX.XX> | Notify QSEs that the system-wide offer cap has changed for AS, Energy, or both. | All QSEs | 190
41 | MMS | CM-VDI-NOTF | Market Message | Low | Verbal Dispatch Instructions for acknowledgement have been sent for the Resource: <RESOURCE_NAME> | Confirm with a QSE that VDIs were sent for a resource | A QSE | 56
42 | MMS | DAM-ASAWD-RPT | Award Notification | Low | Reports on AS Awards for operating date <MM/DD/YYYY> are available. | Awarded Ancillary Service Offers, specifying Resource, MW, Ancillary Service Type, and price, for each hour of the awarded offer; | A QSE | 6460
43 | MMS | DAM-ASINSUFF-NOTF | Alert | High | Due to AS Insufficiency, DAM market for <MM/DD/YYYY> has reopened for AS offer resubmission. The DAM market will close today at <HH:MM>. | ERCOT shall declare an Ancillary Service insufficiency and issue an Alert under Section 6.5.9.3.3, Alert. | All QSEs | 0
44 | MMS | DAM-ASINSUFF-RPT | QSE Data Available | Low | Reports on AS Insufficiency for operating date <MM/DD/YYYY> are available. | Notify QSEs that AS Insufficiency reports are available | All QSEs | 0
45 | MMS | DAM-ASMCPC-RPT | QSE Data Available | Low | Reports on AS MCPC for operating date <MM/DD/YYYY> are available. | Notify QSEs that AS MCPC reports are available | All QSEs | 6080
46 | MMS | DAM-ASOBL-RPT | QSE Data Available | Low | Reports on AS obligation for operating day <MM/DD/YYYY> are available | By 0600 of the Day-Ahead, ERCOT shall notify each QSE of its Ancillary Service Obligation for each service and for each hour of the Operating Day | A QSE | 6270
47 | MMS | DAM-CLOSE-NOTF | Market Message | Low | DAM has closed for <MM/DD/YYYY> | Notify QSEs that the DAM has closed | All QSEs | 7030
48 | MMS | DAM-CRRAWD-RPT | Award Notification | Low | Reports on CRR Awards for operating date <MM/DD/YYYY> are available. | Awarded CRR Offers (PTP Options and PTP Options with Refund), specifying CRR identifier(s), number of CRRs in MW, source and sink Settlement Points, and price, for each Settlement Interval of the awarded offer; and | A QSE | 6270
49 | MMS | DAM-DSRLDTEL-NOTF | Submission Warning | Med | DSR Load Telemetry Notification: DSR Load Telemetry is lost for more than <MIN> mins | Notify QSE that their DSR Load signal has been lost, which results in suspension of DSR output schedule validation. (This alert will be generated as often as every 5 minutes). | A QSE | 1927
50 | MMS | DAM-ENGYAWD-RPT | Award Notification | Low | Reports on Energy Awards for operating date <MM/DD/YYYY> are available. | Awarded Energy Only Bids | A QSE | 6460
51 | MMS | DAM-P2VAL-ERR | Market Message | Med | Phase2 Validation has failed for the date: <MM/DD/YYYY>, type: <DATA_TYPE>. Please find the details in the report <REPORT_NAME>. | Notify QSEs that the Phase 2 validation has failed. | A QSE | 99
52 | MMS | DAM-P2VAL-NOTF | Market Message | Low | Phase2 Validation has completed for the date: <MM/DD/YYYY> | Notify QSEs that the Phase 2 validation (for credit validation, etc) has completed. | All QSEs | 6270
53 | MMS | DAM-PTPAWD-RPT | Award Notification | Low | Reports on PTP Obligation Awards for operating date <MM/DD/YYYY> are available. | Awarded PTP Obligation Bids, number of PTP Obligations in MW, source and sink Settlement Points, and price for each Settlement Interval of the awarded bid. | A QSE | 6270
54 | MMS | DAM-RECLOSE-NOTF | Market Message | Low | DAM has closed due to AS Insufficiency for <MM/DD/YYYY>. | Notify QSEs that the DAM has closed again after reopening for AS insufficiency. | All QSEs | 0
55 | MMS | DAM-TPAWD-RPT | Award Notification | Low | Reports on 3Part Awards for operating date <MM/DD/YYYY> are available. | Awarded DAM Energy Bids, specifying MWh, Settlement Point, and Settlement Point Price for each hour of the awarded bid; | A QSE | 6270
56 | MMS | DRUC-AWD-RPT | RUC Commitment | Low | Reports on DRUC Awards for operating date <MM/DD/YYYY> are available. | ERCOT shall review the RUC-recommended Resource commitments to assess feasibility and shall make any changes that it considers necessary, in its sole discretion. ERCOT shall notify each QSE which of its Resources have been committed as a result of the RUC process. | A QSE | 5890 | Update text to: DRUC was published xx/xx/xxxx.
57 | MMS | DRUC-CLOSE-NOTF | Market Message | Low | DRUC has closed for <MM/DD/YYYY> | Notify QSEs that the DRUC has closed | All QSEs | 6270
58 | MMS | HRUC-AWD-RPT | RUC Commitment | Low | Reports on HRUC Awards for operating date <MM/DD/YYYY> hr <XX> are available. | ERCOT shall review the RUC-recommended Resource commitments to assess feasibility and shall make any changes that it considers necessary, in its sole discretion. ERCOT shall notify each QSE which of its Resources have been committed as a result of the RUC process. | A QSE | 148580 | Update text to: HRUC was published xx/xx/xxxx.
59 | MMS | SASM-ASAWD-RPT | Market Message | Low | Reports on SASM Awards for SASM ID <YYYYMMDDHHMMSS> from operating date <MM/DD> hour <HH> through operating date <MM/DD/HH> are available. | Notify each QSE of its awarded Ancillary Service Offer quantities in each SASM, specifying Resource, Ancillary Service type, SASM MCPC, and first and last hours of the awarded offer. | All QSEs | 4180
60 | MMS | SASM-ASMCPC-RPT | QSE Data Available | Low | Reports for SASM AS MCPC for SASM ID <YYYYMMDDHHMMSS> from operating date <MM/DD> hour <HH> through operating date <MM/DD/HH> are available. | Notify QSEs that SASM MCPC reports are available | All QSEs | 4370
61 | MMS | SASM-ASOBL-RPT | Market Message | Low | Reports on SASM Obligation for SASM ID <YYYYMMDDHHMMSS> from operating date <MM/DD> hour <HH> through operating date <MM/DD> hour <HH> are available. | Notify QSEs of any additional Ancillary Service Obligation, allocated to each LSE and aggregated to the QSE level. | A QSE | 0
62 | MMS | SASM-CLOSE-NOTF | Market Message | Low | SASM has closed for Self AS submission. | Notify QSEs that SASM has closed for AS submission | All QSEs | 0
63 | MMS | SASM-OPEN-NOTF | Market Message | Low | SASM has opened for SASM ID <YYYYMMDDHHMMSS> for Self AS submission. SASM will close at <HH:MM>. | Notify all QSEs of intent to procure additional Ancillary Services. | All QSEs | 0
64 | MMS | SASM-STDYPER-NOTF | Market Message | Low | SASM study period for SASM ID <YYYYMMDDHHMMSS> set from <MM/DD> hour <HH> to <MM/DD> hour <HH>. |  | All QSEs | 4560
65 | MMS | SCED-ADJPER-FAIL | Submission Warning | Med | End of Adjustment Period: Output Schedule Validation FAILED for Hour:<HH> and Date: <MM/DD/YYYY>,. Please find the details in the report <REPORT_NAME>. | If a valid Energy Offer Curve or an Output Schedule does not exist for a Resource that has a status of On-Line at the end of the Adjustment Period, then ERCOT shall notify the QSE and set the Output Schedule equal to the then current telemetered output of the Resource until an Output Schedule or Energy Offer Curve is submitted in a subsequent Adjustment Period. | A QSE | 11
66 | MMS | SCED-ADJPER-WARN | Submission Warning | Med | End of Adjustment Period: Reported warning(s) for Hour: <HH> and Date: <MM/DD/YYYY> Please find the details in the report <REPORT_NAME>. | MMS hourly process that checks for Output Schedule ramp rate and HSL/LSL violations for the hour interval that is at the end of the Adjustment Period. | A QSE | 5649 | Going to report and the report is that all conditions are good. Need to look into report issue. Adjustment Period Report in the Market Manager. Looking for a msg when conditions are not good and the report to detail that information.
67 | MMS | SCED-TELOS-NOTF | Submission Warning | Med | Telemetered Output Schedule Notification: Output Schedule for Resource: <RESOURCE_NAME> | If a valid Output Schedule does not exist for a Resource that has a status of On-Line Dynamically Scheduled Resource at the time of SCED execution, then ERCOT shall notify the QSE and set the Output Schedule equal to the telemetered output of the Resource until a revised Output Schedule is validated. | A QSE | 2386
68 | MMS | SCED-TWOHR-FAIL | Submission Warning | Med | Two Hour Notification: Check FAILED due to missing Output Schedules/Energy Offer Curves for Resource: <RESOURCE_NAME>, Hour: <HH> and Date: <MM/DD/YYYY> | Notify the QSE that an Energy Offer Curve or Output Schedule has not yet been submitted for a Resource as a reminder that one of the two must be submitted by the end of the Adjustment Period | A QSE | 2871
69 | MMS | SCED-TWOHR-FAIL | Submission Warning | Med | Two Hour Notification: Output Schedule Validation FAILED for Hour: <HH> and Date: <MM/DD/YYYY>. Please find the details in the report MP_S_OUTSCHED_TwoHrNotif_<HH>. |  | A QSE | ? | this looks similar to line 70. is the only difference the reference to the link of the report? Recommend to turn off one.
70 | MMS | SCED-TWOHR-WARN | Submission Warning | Med | Two Hour Notification: Reported warning(s) for Hour: <HH> and Date: <MM/DD/YYYY> Please find the details in the report <REPORT_NAME>. | MMS hourly process that checks for Output Schedule ramp rate and HSL/LSL violations for the hour interval two hours from current time. | A QSE | 5679 | Going to report and the report is that all conditions are good. Need to look into report issue. Adjustment Period Report in the Market Manager. Looking for a msg when conditions are not good and the report to detail that information.
71 | MMS | WRUC-COMP-NOTF | Market Message | Low | WRUC has completed for mm/dd/yyyy. | Notify QSEs that the WRUC has completed. | All QSEs | 0
72 | Notice Builder | N/A | Advisory | Medium | ERCOT is issuing an Advisory due to adjusted responsive reserve being below 3000 MW | Adjusted Responsive Reserve < 3000 MW | All MPs(Public) | 9794
73 | Notice Builder | N/A | Advisory | High | ERCOT is issuing an Advisory due to adjusted responsive reserve being below 2500 MW | Adjusted Responsive Reserve < 2500 MW | All MPs(Public)
74 | Notice Builder | N/A | Alert | High | Change in GTL found. Please review. Note: this will link to a page on MIS. Link not available yet. | Change in GTL | All MPs | 0
75 | Notice Builder | N/A | Alert | High | ERCOT has extended the DAM for Operating Day [mmm dd yyyy].until [hh:mm:z],due to <reason text>.Please < interim requirements> | DAM Extension | All QSEs | 0
76 | Notice Builder | N/A | CRR | High | Bid submissions for the [Month or Year][monthly or annual] CRR auction will be accepted starting on [mmm dd yyyy].Details are posted on ERCOT.com | CRR Auction Bid Submissions | All MPs(public) | 0
77 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z] ERCOT declared EEA Level 1 of the Energy Emergency Alert (EEA). | EEA Level 1 | All MPs(Public) | 3956
78 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z] ERCOT declared EEA Level 2A of the Energy Emergency Alert (EEA). | EEA Level 2A | All MPs(Public)
79 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z]ERCOT deployed Group 1 of Load Resources. | Deployment of Group 1 Load Resources | All MPs(Public) |  | ERCOT has removed this message
80 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z]ERCOT deployed Group 2 of Load Resources. | Deployment of Group 2 Load Resources | All MPs(Public) |  | ERCOT has removed this message
81 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z]ERCOT deployed Group 1 and 2 of Load Resources. | Deployment of Group 1 and 2 Load Resources | All MPs(Public) |  | ERCOT has removed this message
82 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z]ERCOT declared EEA Level 2B of the Energy Emergency Alert (EEA). | EEA Level 2B | All MPs(Public)
83 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z]ERCOT declared EEA Level 3 of the Energy Emergency Alert (EEA). | EECP Level 3 | All MPs(Public) |  | update notice description at ERCOT to say EEA Level 3
84 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z]ERCOT moved from EEA Level 3 to EEA Level 2B | EEA Level 3 to EEA Level 2B | All MPs(Public)
85 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z]ERCOT moved from EEA Level 2B to EEA Level 2A. | EEA Level 2B to EEA Level 2A | All MPs(Public)
86 | Notice Builder | N/A | Emergency Notice | High | At [hh:mm:z]ERCOT moved from EEA Level 2A to EEA Level 1. | EECP Step 2 to Step 1 | All MPs(Public) |  | update notice description at ERCOT to say EEA Step 2 to Step 1
87 | Notice Builder | N/A | Emergency Notice | High | ERCOT has declared the DAM process invalid for Operating Day [mmm dd yyyy]due to <reason text>. Please <required schedules and trades during the Adjustment Period.> | DAM Invalid | All QSEs
88 | Notice Builder | N/A | Emergency Notice | High | ERCOT has declared an Emergency due to the failure of the SCED process, starting at [hh:mm:z]. | SCED Failure | All MPs
89 | Notice Builder | N/A | OCN | Low | At [hh:mm:z]on [mmm dd yyyy],ERCOT will perform a site failover of its Energy and Market Management Systems from [hh:mm:z]through [hh:mm:z].During this time, market communications will be unavailable for about 15 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. This event will be preceded by a hot-line call shorty before the start of the failover. | EMS Site Failover | All MPs(Public) | 12918
90 | Notice Builder | N/A | OCN | Medium | ERCOT is issuing an OCN for a projected reserve capacity shortage for hours ending [hh:mm:z]through [hh:mm:z].ERCOT is requesting all QSEs to update their COPs. | Capacity Insufficiency | All MPs
91 | Notice Builder | N/A | OCN | Low | The <DcTie Name> DC Tie will be unavailable from [mmmddyyyy] through [mmmddyyyy] due to a planned outage. | DC Tie Outage | All MPs(Public)
92 | Notice Builder | N/A | Operational Information, OCN, Advisory, Watch, Emergency, AS Postings or Violations | High/Medium/Low | Custom text – actual text entered by operator based on notice. | Free form notices | All MPs(Public) / All QSEs | Undetermined
93 | Notice Builder | N/A | Planning | High | The Electrical Bus [bus name]contained within [hub bus name]has been removed due to reflected changes in the Transmission Grid as submitted by [NOMCR owner]. and is effective [mmm dd yyyy].The Electrical Bus will be excluded from pricing calculations after removal | Electrical Bus Removal | All MPs(public) | 0
94 | Notice Builder | N/A | Settlements | High | The following data will not be available on the schedulThe following data will not be available on the scheduled date: (List all that are appropriate*).The [RTM or DAM]for Operating Day [mmm dd yyyy]will be resettled. View details. * List • Each Settlement Invoice for the DAM • Payments for the DAM • Each Late Fee Invoice for the DAM • Payments for DAM Late Fee Invoices • Settlement Invoice for the RTM • Payments for the Real-Time Market • Late Fee Invoice for the RTM • Payments for RTM Late Fee Invoices • RTM Uplift Invoice • Payments for RTM Uplift Invoices • Congestion Revenue Rights (CRR) Auction Invoic • Payments for CRR Auction Invoices • CRR Auction Revenue Distribution Invoice • Payments for CRR Auction Revenue Distribution Invoices • Each CRR Balancing Account Invoic • Payments for CRR Balancing Account Invoice • Settlement and Billing Disputes for each scheduled Settlement Statement. | Settlements Delay | All MPs(Public) | 416 | look at notice text and update the sentence that is chopped off.
95 | Notice Builder | N/A | Settlements | High | The <Market> Statement for Operating Day <Operating Day> will be resettled. (This notice is undergoing a change to include additional fields rather than the View Details link.) | Resettlement Notice | All MPs(Public)
96 | Notice Builder | N/A | Settlements | High | The True-Up Statement for Operating Day [ ]has been delayed. This delay is due to [ ].ERCOT expects to issue the Real-Time Market True-Up Statement on [ ]. | Delay of RTM True-Up | All MPs(Public)
97 | Notice Builder | N/A | Settlements | High | The True-Up Statement for Operating Day [mmm dd yyyy]will be posted on [mmm dd yyyy]. | RTM True-Up Settlement Notice | All MPs(Public)
98 | Notice Builder | N/A | Watch | High | FR3061 DAM-ASINSUFF-NOTF Due to AS Insufficiency, DAM market for MM/DD/YYYY has reopened for AS offer resubmission. The DAM market will close today at HH:MM. Note: This notice is not automatically sent and requires operator intervention. | AS Insufficiency | All QSEs | 3536
99 | new |  |  |  |  | Notify when SCED is complete. This triggers the reporting for the prices. This will come out every 5 minutes. |  |  | ERCOT will plan for a release date for turning on this existing internal notice to be sent to MPs. ERCOT will send a market notice with this release date.
100 | new |  |  |  |  | Notify when SPP are available to trigger the market for report downloads |  |  | While this would be addressed in a longer term solution for pushing data from ERCOT to the market, look at adding a notification of when SPPs are available for download to limit the amount of download requests.
101 | new |  |  |  |  | Notify when non-spin deployments occur. Send to all MPs. |  |  | New

## Luminant-to eliminate
ERCOT_ID | ERCOT_TYPE | DESCRIPTION | LUMINANT_ID | Luminant Comments
DRUC-AWD-RPT | RUC Commitment | ERCOT shall notify each QSE which of its Resources have been committed as a result of the RUC process. | DRUC - Awards | Send an Alert when the QSE's unit is RUC'd, not a message to look at a report
HRUC-AWD-RPT | RUC Commitment | ERCOT shall notify each QSE which of its Resources have been committed as a result of the RUC process. | HRUC - Awards | Send an Alert when the QSE's unit is RUC'd, not a message to look at a report
SCED-TWOHR-WARN | Submission Warning | MMS hourly process that checks for Output Schedule ramp rate and HSL/LSL violations for the hour interval two hours from current time. | SCED - OS has invalid Ramp Rate and/or HSL/LSL | The report that this Alert references does not make sense.
CM-ADJCLOSE-NOTF | Market Message | Notify QSEs that the adjustment period window has closed | Adjustment Period Closed | Alert is meaningless
CM-ADJOPEN-NOTF | Market Message | Notify QSEs that the adjustment period window has opened | Adjustment Period Open | Alert is meaningless
CM-OPHRCLOSE-NOTF | Market Message | Notify QSEs that the Market has closed | Operating Hour Closed | Alert is meaningless
CM-ASTRD-NOTF | Reported Trade | When an Ancillary Service Trade is reported to ERCOT, ERCOT shall notify the counterparty to the trade. | Trade Confirm - A/S | Recommend elimation to decrease message traffic
CM-CAPTRD-NOTF | Reported Trade | When a Capacity Trade is reported to ERCOT, ERCOT shall notify the counterparty to the trade. | Trade Confirm - Capacity | Recommend elimation to decrease message traffic
CM-ENGTRD-NOTF | Reported Trade | When an Energy Trade is reported to ERCOT, ERCOT shall notify the counterparty to the trade. | Trade Confirm - Energy | Recommend elimation to decrease message traffic
CM-CONSCK-FAIL | COP Warning | Five minutes before the end of each hour, ERCOT shall identify inconsistencies between the telemetered Resource Status and the Resource Status stated in the COP for that Resource in the next hour. On detecting an inconsistency, ERCOT shall provide a notice of inconsistent Resource Status to the QSE using the Messaging System | COP for next hour does not match telemetry | Recommend elimation to decrease message traffic
RLCHSLAS | TELEMETRY | HSL <= Sum of Reg-Up Responsibility, Responsive Schedule and Non-Spin schedule | A/S Allocation Issue : HSL <= A/S Allocation | Seeing many of these when unit status is ON with no AS | Telemetry
RLCSUSMW | TELEMETRY | If the HDL = LDL = Actual Generation and Resource Status not ON TEST, or OFF alarm the QSE operator to verify data telemetry used by RLC. | Unit not available for SCED dispatch | This Alert should not be issued for units which are OUT