ERCOT Operations Report

March 2011 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 3/3/2011 11:17 | 59.842 | 88 | Unit trip with 440 MW |
| 3/3/2011 19:03 | 60.133 | 150 | Out of DRS. |
| 3/8/2011 23:06 | 59.898 | 16 | Gen Deviation -500 in 2 mins |
| 3/9/2011 5:57 | 60.107 | 108 | Gen Deviation +1100 in 3 mins |
| 3/14/2011 5:58 | 60.174 | 400 | Gen Deviation +1300 in 4 mins |
| 3/14/2011 6:09 | 59.801 | 164 | Multiple Unit trips with 910 MW |
| 3/14/2011 7:08 | 59.855 | 64 | Multiple Unit trips with 651 MW |
| 3/14/2011 22:02 | 59.851 | 252 | Gen Deviation -1500 in 5 mins; out of URS |
| 3/15/2011 5:59 | 60.148 | 291 | Gen Deviation +1400 in 5 mins |
| 3/16/2011 5:56 | 60.110 | 88 | Gen Deviation +700 in 2 mins |
| 3/16/2011 20:45 | 59.867 | 12 | Unit trip with 420 MW |
| 3/16/2011 23:06 | 59.883 | 156 | Gen Deviation -800 in 3 mins |
| 3/17/2011 5:56 | 60.109 | 36 | Gen Deviation +800 in 3 mins |
| 3/17/2011 22:03 | 59.877 | 88 | Gen Deviation -700 in 1 min |
| 3/19/2011 22:05 | 59.891 | 18 | Gen Deviation -400 in 4 mins |
| 3/22/2011 15:46 | 59.886 | 16 | Unit ran back by 400 MW; out of URS |
| 3/23/2011 14:46 | 59.719 | 12 | Unit trip with 1014 MW |
| 3/23/2011 14:48 | 59.861 | 104 | Unit trip with 390 MW |
| 3/24/2011 13:59 | 59.796 | 104 | Unit trip with 570 MW |
| 3/25/2011 4:05 | 59.896 | 36 | Gen Deviation -500 in 2 mins |
| 3/25/2011 16:13 | 59.814 | 100 | Multiple Unit trips with 586 MW |
| 3/25/2011 22:00 | 59.879 | 204 | Gen Deviation -1200 in 5 mins |
| 3/26/2011 19:50 | 59.875 | 16 | Unit trip with 500 MW |
| 3/27/2011 0:01 | 59.896 | 16 | Gen Deviation -500 in 2 mins |
| 3/27/2011 22:01 | 59.893 | 96 | Gen Deviation -600 in 2 mins |
| 3/28/2011 22:05 | 59.868 | 156 | Gen Deviation -500 in 1 min; out of URS |
| 3/29/2011 6:43 | 59.753 | 72 | Unit trip with 750 MW |
| 3/30/2011 5:57 | 60.129 | 152 | Gen Deviation +700 in 2 mins; out of DRS |
| 3/31/2011 12:21 | 59.861 | 56 | Unit trip with 420 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 3/14/11 22:05:10 | 3/14/11 22:10:38 | 0:05:28 | 319 |  |
| 3/17/11 22:04:57 | 3/17/11 22:11:53 | 0:06:56 | 400 |  |
| 3/23/11 14:46:57 | 3/23/11 14:51:36 | 0:04:39 | 405 |  |
| 3/25/11 16:13:39 | 3/25/11 16:16:58 | 0:03:19 | 330 |  |

RUC Capacity Purchases

| Weather Zone | Unit Days |
| --- | --- |
| COAST | 8 |
| EAST | 1 |
| FAR WEST | 15 |
| NORTH CENTRAL | 7 |
| SOUTH | 10 |
| SOUTH CENTRAL | 20 |
| Grand Total | 61 |

SCED Congestion Management Activity

Congestion affected by outages Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Bluff Creek Auto T2_H ,T2_L & T2_T | Nicole - Oak Creek CSW 138Kv | 25 |
| Fort Stockton - Barilla 138kV | Barilla - Fort Stockton Switch 69 kV | 12 |
| Willow Valley Switch - Exxon Sharon Ridge 138 kV | Ackerly Vealmoor Switch - Ackerly 69 kV | 9 |
| Odessa North - Odessa Basin Switch 69kV | Holt Switch - Ector Shell Tap 69kV | 8 |
| Pawnee - Lon Hill 345 kV | Sinton - Skidmore 138 kV | 7 |
| Base case | No Trees Switch - No Trees Wind farm 138 kV | 4 |
| Gail - Key Sub 138 kV | Ackerly Vealmoor Switch - Ackerly 69 kV | 4 |
| Holt Switch-Amoco North Cowden T-N Cowden Amoco-Moss Switch | Odessa North 138/69kV AXFMR1 | 3 |
| DCKT Singleton - Tomball & Roans Prairie 345kV | Singleton - O'brien 345kV | 2 |
| Aspermont - Spur 138 kV | Spur 138/69 kV AXFMR | 2 |
| Odessa EHV Switch - Morgan Creek SES & Quail Switch 345kV | Ackerly Vealmoor Switch - Ackerly 69kV | 2 |
| Gail - Key Sub 138 kV | Ackerly - Ackerly Lyntegar 69 kV | 2 |
| Graham SES - Long Creek & Cook Field 345kV | Leon Switch - Putnam 138 kV | 2 |
| Lon Hill 345/138 kV AXFMR | Nelson Sharpe - Celanese Bishop 138kV | 2 |
| DCKT Singleton - Tomball & Roans Prairie 345kV | Singleton - Zenith 345kV | 1 |
| Lon Hill - Nelson Sharpe 345 kV | Nelson Sharpe PS | 1 |
| Graham SES - Long Creek & Cook Field 345kV | Bomarton - Seymour 69kV | 1 |
| Morgan Creek SES - Sun Switch 138Kv/6474 | Colorado City - China Grove Switch 69Kv/6685 | 1 |
| Coleto Creek Generator 1 | Blessing - Lolita 138 kV | 1 |
| Royse Switch - Forney Switch 345 kV | Forney Switch 345/138 kV AXFMR 3 | 1 |
| DCKT Calavers - Braunig & Cagnon 345 kV | Calaveras to Skyline 345 kV | 1 |
| STP Units 1 &2 | Blessing - Lolita 138 kV | 1 |
| Lon Hill 345/138 kV AXFMR | Celanese Bishop - Kleberg CSW 138 KV | 1 |
| Ajo - Rio Hondo 345 kV | Celanese Bishop - Kleberg CSW 138 KV | 1 |
| Oklaunion - Abilene Mulberry Creek 345 kV | Lake Pauline 138/69 kV AXFMR | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 26 |
| Valley Import | 3 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

03/28 	Allen Switch – Ben Davis 138 kV SPS modified.

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 03/25/2011 | Transmission and Security Desk V1 Rev5 | 527 |
| 03/25/2011 | Reliability Unit Commitment Desk V1 Rev4 | 526 |
| 03/25/2011 | Resource Desk V1 Rev4 | 525 |
| 03/25/2011 | Real Time Desk V1 Rev5 | 524 |
| 03/25/2011 | Shift Supervisor Desk V1 Rev523 | 523 |
| 03/25/2011 | DC Tie Desk V1 Rev3 | 522 |

## Load Shed Incidences

None

EEA

03/23 14:50   	ERCOT issued an EEA Level 1. ERCOT cancelled EEA Level 1 at 15:23.

System Voltage Problems

None

Application Issues

03/05 10:13 	ERCOT issued an Emergency Notice due to EMS and SCED failure.

Communication Issues

None

## ERCOT peak (Unofficial)

03/23 18:00 40,162 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2008 | 2009 | 2010 | 2011 |
| January | 3.30 | 4.11 | 3.78 | 2.91 |
| February | 3.59 | 3.49 | 3.79 | 3.46 |
| March | 3.29 | 3.24 | 2.24 | 2.02 |
| April | 2.45 | 2.66 | 2.47 | NA |
| May | 3.01 | 2.90 | 2.63 | NA |
| June | 2.81 | 2.89 | 2.84 | NA |
| July | 2.55 | 2.83 | 2.39 | NA |
| August | 3.66 | 3.07 | 2.29 | NA |
| September | 4.99 | 3.68 | 3.14 | NA |
| October | 2.79 | 2.92 | 2.37 | NA |
| November | 2.60 | 1.93 | 3.46 | NA |
| December | 4.54 | 3.70 | 2.60 | NA |
| Annual Average | 3.29 | 3.11 | 2.83 | 2.79 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 3/2/2011 | 3:43 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1100-2100. |
| 3/3/2011 | 11:41 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/4/2011 | 6:45 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1300-1700. |
| 3/4/2011 | 10:15 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/6/2011 | 6:22 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 0900-1500. |
| 3/8/2011 | 6:30 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1100-2100. |
| 3/9/2011 | 1:31 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1900-2400. |
| 3/9/2011 | 10:12 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/10/2011 | 6:05 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 0800-2000. |
| 3/10/2011 | 7:00 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/12/2011 | 3:24 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1400 -2000. |
| 3/12/2011 | 12:48 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/13/2011 | 3:08 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 2000-2100. |
| 3/13/2011 | 13:48 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/14/2011 | 12:42 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 2000-2400. |
| 3/15/2011 | 11:48 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 2100-2200. |
| 3/17/2011 | 12:17 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1600-2400. |
| 3/18/2011 | 3:00 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1600-2400. |
| 3/18/2011 | 14:15 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/19/2011 | 22:22 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/20/2011 | 20:00 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/22/2011 | 7:15 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/23/2011 | 12:26 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1700-1900. |
| 3/23/2011 | 15:45 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/24/2011 | 7:05 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/24/2011 | 9:20 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1700-2200. |
| 3/25/2011 | 7:01 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/25/2011 | 14:02 | ERCOT is issuing an OCN for a Projected Reserve Capacity Shortage for HE 1600-1800. |
| 3/25/2011 | 7:01 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/25/2011 | 14:00 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1600-1800. |
| 3/26/2011 | 3:00 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1700-1900. |
| 3/26/2011 | 11:42 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/27/2011 | 22:17 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/28/2011 | 7:02 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/29/2011 | 22:10 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 3/31/2011 | 16:10 | ERCOT issued an Advisory due to PRC below 3000 MW. |

Transmission Watch

03/04 16:27   	ERCOT issued transmission watch for the post contingency loss of Lobo to San Miguel 345 kV line overloads Freer to San Diego 69KV line. Cancelled the watch at 18:12.

Texas RE Event Analysis

03/14 06:09	ERCOT experienced a simultaneous loss of one 345 KV Bus and two generating units (resulting in the loss of approximately 922 MW within the first minute of the event) due to a thunderstorm.

03/14 07:08	ERCOT experienced a simultaneous loss of two 345 KV lines and five generating units (resulting in the loss of approximately 651 MW within the first minute of the event). A root-cause evaluation is currently on-going to determine the cause of the trip.

03/23 14:46	ERCOT experienced a simultaneous loss of one 345 KV Bus, causing the loss of four 345 KV lines, one 345/138 KV Autotransformer and two combined cycle Resources (resulting in the loss of approximately 1,014 MW within the first minute of the event). At 14:50 ERCOT implemented Level 1 of its Energy Emergency Alert (EEA) as PRC dropped below 2,300 MW. ERCOT requested 1,873 MW of Non-Spin at 14:58. By 15:14 PRC was above 3,000 MW and EEA Level 1 was cancelled at 15:23. This event caused a frequency deviation of 0.3 Hz (59.700 Hz) at 14:46:50 per ERCOT ISO High-Speed Frequency Recorder Data. Frequency recovered within 5 minutes and 40 seconds to 60 Hz at 14:52:30.

03/25 16:13	ERCOT experienced a simultaneous loss of four generating units and one unit run-back (resulting in the loss of approximately 586 MW within the first minute of the event). Investigation is currently on-going.

03/30 04:02	ERCOT experienced a simultaneous loss of three 138 KV lines and one DC-Tie. Investigation is currently on-going.