## Slide 1: PDCWG Report to ROS
April 11, 2011
Sydney Niemeyer

## Slide 2
CPS1 12 Month Rolling Average = 149.97
The March CPS1 score was 141.34

## Slide 4: RMS1 of ERCOT Frequency and Frequency Profile
RMS1 evaluation of ERCOT frequency, CPS1 by day and the frequency profile results for March, 2011 are not available at this time.
  Since ERCOT discontinued the telemetry of scheduled frequency to QSEs in Nodal, the process of inserting Time Error Corrections into the evaluation process is now manual. If time is available these graphs will be provided at a later date.

## Slide 5: Frequency Events Reviewed
Thursday Mar 3, 2011 @ 11:17
  441 MW -468 MW/0.1 Hz 72% of Bias -104.3 µHz/sec/MWloss
Monday Mar 14, 2011 @ 06:09
  924 MW -445 MW/0.1 Hz 68% of Bias -117.7 µHz/sec/MWloss
Monday Mar 14, 2011 @ 07:08
  487 MW -383 MW/0.1 Hz 59% of Bias -145.7 µHz/sec/MWloss

## Slide 12: Follow-up of Feb 2, 2011 Frequency Event
Following PDCWG review of Resource performance in delivery of Primary Frequency Response during the 02:18 am and 05:14 am events, Resources that provided less than minimum levels of PFR were contacted by ERCOT.
Based on responses from these QSE’s/Resources the next two slides present the expected level of improvement in performance the Interconnection would have seen on these two events.

## Slide 13: Feedback from Resources Contacted in Regard to PFR Performance during the 05:14 am event Feb 2, 2011
Average Interconnection Frequency Response -347.5 MW/0.1 Hz.
Corrective action would have resulted in a 12.5 to 18.9 % improvement in Interconnection frequency response on this event. Interconnection frequency response would have been -391.2 to -413.2 MW/0.1 Hz with these improvements instead of the actual measured -347.5 MW/0.1 Hz.

## Slide 14: Feedback from Resources Contacted in Regard to PFR Performance during the 02:18 am event Feb 2, 2011
Average Interconnection Frequency Response -452.5 MW/0.1 Hz.
Corrective action would have resulted in a 40.5 to 75.4 % improvement in Interconnection frequency response on this event. Interconnection frequency response would have been -636.0 to -793.9 MW/0.1 Hz with these improvements instead of the measured -452.5 MW/0.1 Hz.
One Resource providing RRS stated that their Resource could not meet the minimum frequency response requirement.

## Slide 15: Summary
The Feb 2 05:14 am event had fewer generators with spinning reserve that could be evaluated so fewer generators had measured low or withdrawn performance.
The PDCWG, through ERCOT, will continue to communicate observed Resource Primary Frequency Response performance problems with their QSE’s and work with them to improve their performance.
The PDCWG will meet on May 4, 2011 at the ERCOT Met Center.