| NPRR Number | 324 | NPRR Title | Conductor/Transformer Transmission Facility Rating |
| --- | --- | --- | --- |
| Date |  | February 23, 2011 |  |
| Submitter’s Information |  |  |  |
| Name |  | David Bogen |  |
| E-mail Address |  | dbogen@oncor.com |  |
| Company |  | Oncor Electric Delivery |  |
| Phone Number |  | (214) 743-6735 |  |
| Cell Number |  |  |  |
| Market Segment |  | Investor Owned Utility |  |

Comments

In determining the 15 -Minute Rating, this Nodal Protocol Revision Request (NPRR) requires that only a 90% pre-load be used for this calculation. The Transmission Service Provider (TSP) Rating Methodology document that Oncor has filed with ERCOT specifies that Oncor uses an 84% pre-load for this calculation. For a more detailed explanation of the Oncor’s rating methodology, see https://mis.ercot.com/pps/tibco/mis/Pages/Grid+Information/Long+Term+Planning. (Look under Network Operations Model/TSP Rating Methodology.) Oncor made this determination based on historical statistical analysis of the loading of Oncor’s transmission system. Oncor would like to see this NPRR be modified such that it will allow for a preloading of up to 90% so the TSPs can develop ratings more appropriate for their transmission system to provide better utilization of the transmission system.

If this modification is not made Oncor will be required to resubmit ratings for all transmission lines and autotransformers. The resubmitted 15-Mminute Ratings would be lower than the current information that has been submitted to ERCOT.

Revised Proposed Protocol Language

## 2.1	DEFINITIONS

Rating

Conductor/Transformer Rating

The two hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The conductor or transformer can operate at this rating for two hours without violation of National Electrical Safety Code (NESC) clearances or equipment failure.

Emergency Rating

The two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure.

15-Minute Rating

The 15 minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading up to 90% of the Normal Rating.  The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading up to 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

Normal Rating

The continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

## 2.2	ACRONYMS AND ABBREVIATIONS

NESC	National Electrical Safety Code

- 3.10.7.1.1	Transmission Lines

(1)	ERCOT shall model each transmission line that operates in excess of 60 kV.

(2)	For each of its transmission lines operated as part of the ERCOT Transmission Grid, each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information consistent with the ratings methodology prescribed in the ERCOT Operating Guides:

(a)	Equipment owner(s);

(b)	Equipment operator(s);

(c)	Transmission Element name;

(d)	Line impedance;

(e)	Normal Rating, Emergency Rating, 15-Minute Rating, and Conductor/Transformer Rating; and

(f)	Other data necessary to model Transmission Element(s).

(3)	The TSP and Resource Entity may submit special transfer limits and stability limits for secure and reliable grid operations for ERCOT approval.  ERCOT has sole decision-making authority and responsibility to determine the limits to be applied in grid operations.

(4)	The TSP and Resource Entity may implement protective relay and control systems and set values appropriate to de-energize faulted equipment and meet the TSP and Resource Entity obligations for public or employee safety, and when necessary to prevent in-service or premature equipment failure consistent with Good Utility Practice and accepted industry standards.  The TSP and Resource Entity shall include those limits when providing ERCOT with ratings or proposed transfer limits.

(5)	The Network Operations Model must use rating categories for Transmission Elements as defined in the ERCOT Operating Guides.