| NPRR Number | 304 | NPRR Title | Removal of Frequency Bias Methodology Approval Requirement |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approved |
| Date of Decision |  | April 19, 2011 |  |  |
| Effective Date |  | May 1, 2011 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Protocol Section Requiring Revision |  | 6.5.7.6.1, LFC Process Description |  |  |
| Requested Resolution |  | Normal |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) removes the requirement for ERCOT to develop a methodology, subject to Technical Advisory Committee (TAC) approval, to determine the optimal frequency bias for given system conditions. |  |  |
| Reason for Revision |  | The responsibility for determining a methodology for frequency bias falls upon ERCOT pursuant to its roles as North American Electric Reliability Corporation (NERC) Balancing Authority and Reliability Coordinator for the ERCOT Region. See NERC Reliability Standard BAL-003-0.1b, Frequency Response and Bias. ERCOT will continue to consider input from the Performance, Disturbance, Compliance Working Group (PDCWG) or directly from TAC regarding the frequency bias methodology and the bias number calculated pursuant thereto. However, the requirement to obtain TAC approval is being eliminated to ensure that the Nodal Protocols provide ERCOT with the necessary discretion to carry out this Balancing Authority/Reliability Coordinator responsibility. |  |  |
| Overall Market Benefit |  | Clearer definition of responsibilities. |  |  |
| Overall Market Impact |  | None. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR304 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 12/17/10, NPRR304 and an Impact Analysis were posted. - On 1/20/11, PRS considered NPRR304. - On 2/17/11, PRS considered the 1/20/11 PRS Report and Impact Analysis for NPRR304. - On 3/3/11, TAC considered NPRR304. - On 4/19/11, the ERCOT Board considered NPRR304. |  |  |
| PRS Decision |  | On 1/20/11, PRS unanimously voted to recommend approval of NPRR304 as submitted. All Market Segments were present for the vote. On 2/17/11, PRS unanimously voted to endorse and forward the 1/20/11 PRS Report and Impact Analysis for NPRR304 to TAC. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 1/20/11, it was noted that ERCOT has stated that it would continue to consult with TAC and PDCWG regarding the frequency bias methodology if NPRR304 is approved. On 2/17/11, there was no discussion. |  |  |
| TAC Decision |  | On 3/3/11, TAC unanimously voted to recommend approval of NPRR304 as recommended by PRS in the 2/17/11 PRS Report. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 3/3/11, there was no discussion. |  |  |
| Board Decision |  | On 4/19/11, the ERCOT Board approved NPRR304 as recommended by TAC in the 3/3/11 TAC Report. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Clearer definition of responsibilities. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Sandip Sharma |
| E-mail Address | ssharma@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4298 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jonathan Levine |
| E-Mail Address | jlevine@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Proposed Protocol Language Revision

6.5.7.6.1	LFC Process Description

(1)	The LFC system corrects system frequency based on the Area Control Error (ACE) algorithm and Good Utility Practice.

(2)	The ACE algorithm subtracts the actual frequency in Hz from the scheduled system frequency (normally 60 Hz), and multiplies the result by the frequency bias constant of MW/0.1 Hz.  The ACE algorithm then takes that product and subtracts a configurable portion of the sum of the difference between the Updated Desired Base Point and Real-Time net MW output as appropriate.  LFC shall ensure that the total reduction will not exceed the system-wide regulation requirement.  This calculation produces an ACE value, which is a MW-equivalent correction needed to control the actual system frequency to the scheduled system frequency value.

(3)	The LFC module receives inputs from Real-Time telemetry that includes Resource output and actual system frequency.  The LFC uses actual Resource information calculated from SCADA to determine available Resource capacity providing Regulation and RRS services.

(4)	Based on the ACE MW correction, the LFC issues a set of control signals every four seconds to each QSE providing Regulation and, if required, each QSE providing RRS.  Control must be proportional to the QSE’s share of each of the services that it is providing, respecting the QSE’s Resources’ capability to provide regulation control.  Control signals are provided to the QSE using the ICCP data link.  QSEs shall receive an Updated Desired Base Point updated every four seconds by LFC.  ERCOT will provide an Operations Notice of any methodology change to the determination of the Updated Desired Base Point within 60 minutes of the change.

(5)	Each QSE shall allocate its Regulation energy deployment among its Resources to meet a deployment signal, and shall provide ERCOT with the participation factor of each Resource via telemetry in accordance with Section 6.5.7.6.2.1, Deployment of Regulation Service, and Section 6.4.8.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency.  Each QSE’s allocation of Regulation Service to its Resources must be consistent with the telemetry provided under Section 6.5.5.2, Operational Data Requirements.  Each QSE’s allocation of its Regulation energy deployment among its Resources to meet a deployment signal must ensure the participation factors of all its Generation Resources in comparison to all its Controllable Load Resources remains constant.

(6)	If all Reg-Up capacity has been deployed, ERCOT shall use the LFC system to deploy Responsive Reserve on Generation Resources and Controllable Load Resources.  Such Responsive Reserve deployments by ERCOT must be deployed as specified in Section 6.5.7.6.2.2, Deployment of Responsive Reserve Service.

(7)	ERCOT shall settle energy that results from LFC deployment at the Settlement Point Price for the point of injection.  When a QSE deploys Responsive Reserve Service, the QSE shall deploy units consistent with the performance criteria for RRS service in Sections 8.1.1.3.2, Responsive Reserve Service Capacity Monitoring Criteria, and 8.1.1.4.2, Responsive Reserve Service Energy Deployment Criteria.

(8)	The inputs for LFC include:

(a)	Actual system frequency;

(b)	Scheduled system frequency;

(c)	Capacity available for Regulation by QSE;

(d)	Telemetered high and low Regulation availability status indications for each Resource available for Regulation deployments for ERCOT information;

(e)	Resource limits calculated by ERCOT as described Section 6.5.7.2, Resource Limit Calculator;

(f)	Resource Regulation participation factor;

(g)	Capacity available for Responsive Reserve by QSE;

(h)	ERCOT System frequency bias; and

(i)	Telemetered Resource output.

(9)	If system frequency deviation is greater than an established threshold, ERCOT may issue Dispatch Instructions to those Resources not providing Reg-Up or Reg-Down that have Base Points directionally opposite ACE, to temporarily suspend ramping to their Base Point until frequency deviation returns to zero.