| NOGRR Number | 064 | NOGRR Title | QSE Acknowledgement of VSS Dispatch Instructions |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | April 20, 2011 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Guide Section Requiring Revision |  | 2.7.4.1, Maintaining System Voltage |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) revises language in Section 2.7.4.1 to be consistent with paragraph (3) of Section 2.2.10, Generation Resource Response Time Requirements. Section 2.7.4.1 requires Qualified Scheduling Entities (QSEs) to respond within two minutes of receipt of a Dispatch Instruction from ERCOT for Voltage Support Service (VSS) while paragraph (3) of Section 2.2.10 requires a response within five minutes. |  |  |
| Reason for Revision |  | To remove inconsistency between two sections of the Nodal Operating Guides related to the appropriate time period of response by a QSE to a VSS Dispatch Instruction. Furthermore, two minutes is not enough time for a QSE to receive a VSS Dispatch Instruction from ERCOT, then contact the appropriate Generation Resource who then must physically change the voltage at the Generation Resource using whatever means appropriate. This change does not reduce system reliability since existing Nodal Operating Guide language in paragraph (3) of Section 2.2.10 already allows a QSE up to five minutes to respond to a VSS Dispatch Instruction. |  |  |
| Overall Market Benefit |  | Removes ambiguity existing in the Nodal Operating Guides and provides clarity to Market Participants as to the responsibilities of QSEs to respond to VSS Dispatch Instructions. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | None. |  |  |
| Procedural History |  | - On 3/8/11, NOGRR064 was posted. - On 4/2011, the Operations Working Group (OWG) considered NOGRR064. |  |  |
| OWG Decision |  | On 4/20/11, OWG was in consensus to recommend approval of NOGRR064 as revised by OWG. |  |  |
| Summary of OWG Discussion |  | On 4/20/11, the sponsor of NOGRR064 reviewed the proposed language changes, and OWG was in agreement to align the language with the requirements in Section 2.2.10. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Consistency of Nodal Operating Guides. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Henry Durrwachter |
| E-mail Address | hdurrwachter@luminant.com |
| Company | Luminant Energy Company LLC |
| Phone Number | (214) 875-9285 |
| Cell Number | (214) 437-4622 |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sonja B. Mingo |
| E-Mail Address | smingo@ercot.com |
| Phone Number | 512-248-6463 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Proposed Guide Language Revision

2.7.4.1	 Maintaining System Voltage

(1)	ERCOT will maintain a performance log of QSEs acknowledgements of Voltage Support Service (VSS) Dispatch Instructions concerning scheduled voltage or scheduled reactive output requests.  A QSE’s response that is completed in no more than five minutes from the time of issuance of such requests shall be deemed satisfactory.

(2)	ERCOT shall monitor the Automatic Voltage Regulator (AVR), as required in Protocol Section 6.5.5.1, Changes in Resource Status, to assure that it is on and operating automatically at least 98% of the time in which the QSE is providing the Reactive Power supply from Generation Resources required to provide VSS.  The percentage is calculated as:  Time (AVR is on while providing Service) / (Total Time Providing Services) (100%).

(3)	Except under Force Majeure conditions or ERCOT-permitted operation of the Generation Resource, failure of a Generation Resource required to provide VSS to provide either leading or lagging reactive up to the required capability of the unit upon request from a TO or ERCOT may, at the discretion of ERCOT, be reported to the Texas Regional Entity (TRE).

(4)	Except under Force Majeure conditions or ERCOT-permitted operation of the Generation Resource, if a Generation Resource required to provide VSS fails to maintain transmission system voltage at the point of interconnection with the TSP within 2% of the voltage profile while operating at less than the maximum reactive capability of the Generation Resource, ERCOT may, at its discretion, report this to the TRE.

(5)	The TRE will investigate claims of alleged non-compliance and Force Majeure conditions, and address confirmed non-compliance situations.  The TRE will advise the Generation Resource, its QSE, ERCOT, and the TSP planning and operating staffs of the results of such investigations.