## Slide 1: Valley Import Constraint
Resmi Surendran
<number>

## Slide 2: Valley Import Constraint
Range of SFs
  -0.95 to -0.97 in valley area
  0.03 to 0.045 outside valley area
Not a competitive constraint and hence the Resources are moved based on offers capped by higher of Reference LMP & Mitigated Offer Cap curve
Base case constraint and hence has a default Max Shadow Price of $5000/MWh
<number>

## Slide 3: Issue
Highest Shadow Price when not violated is less than $100/MWh (more than 16 hr in the first 4 months)
  Constraint cannot be resolved many times even with all the generation available
South LZ SPP when the constraint is violated ranges from $1500/MWh to $1850/MWh (more than 7 hr in the first 4 months)
  Demand response in majority of that load zone with the high price have no impact to the constraint.
Constraint is manually handled after it has been violated for more than an hour in SCED (roughly 43 hrs in the first 4 months)
<number>

## Slide 4: Potential Long Term Solution
Develop transmission network to support load growth.
Create a Load Zone for Valley to encourage demand participation that has impact on the constraint
<number>

## Slide 5: Short Term Solution
Reduce Max Shadow Price and let the constraint be managed by SCED and provide price signal to encourage new generation development or load participation
  Import from DC tie is limited during peak hours
  Demand participation would be less since the deployment would be for long hours and payments would be based on the South LZ SPP
Revalidate the limit calculations in planning and operations
<number>

## Slide 6: Proposed Max Shadow Price - $350/MWh
Should be able to move existing or new Resources to resolve constraint with out manual action
To fully dispatch the highest capped and bounded offer during non-scarcity intervals
The highest offer from a new resource with no verifiable cost that needs to be moved is
  14.5 * high FIP/ lowest SF = 14.5 *10 /0.95 ~ 150
The highest offer from a new resource with verifiable cost that needs be moved is
  (high Heat Rate * High FIP + corresponding high O&M) * highest multiplier/ lowest SF
  (14 .5*10 + 75 )*1.5/0.95 ~ $350/MWh
<number>

## Slide 7: Hours of Binding/Violation
 | December | January | February | March | sum | violated hrs
Hours active in SCED | 2.8 | 21.5 | 26.9 | 9.3 | 60.5 | 
Hours binding in SCED | 1.3 | 6.0 | 6.8 | 2.1 | 16.3 | 
Hours violated in SCED | 0.0 | 2.1 | 5.2 | 0.0 | 7.3 | 
Hours with Violated & overridden | 0.1 | 3.9 | 39.3 | 0.0 | 43.3 | 50.5
<number>
Active in SCED – Constraint is passed to SCED
Binding in SCED – Constraint is resolved by SCED – Flow = Limit
Violated in SCED – Constraint was not resolved by SCED – Flow > Limit
Violated & Overrriden – LDL was overriden and Flow > Limit
Congestion Cost = (Flow MW * Shadow Price) per 5 min * 1/12

## Slide 8: Congestion Cost
 | December | January | February | March | sum | violated hrs
Hours active in SCED | 2.8 | 21.5 | 26.9 | 9.3 | 60.5 | 
Hours binding in SCED | 1.3 | 6.0 | 6.8 | 2.1 | 16.3 | 
Hours violated in SCED | 0.0 | 2.1 | 5.2 | 0.0 | 7.3 | 
Hours with Violated & overridden | 0.1 | 3.9 | 39.3 | 0.0 | 43.3 | 50.5
<number>
SP*MW Flow | December | January | February | March | Sum | Sum in SCED
VALIMP binding in SCED | $3,089.05 | $56,224.85 | $33,959.97 | $2,011.26 | $95,285.14 | $46,736,118.47
VALIMP violated in SCED @SP5000 | $0.00 | $11,831,250.00 | $34,809,583.33 | $0.00 | $46,640,833.33 | 
Violated & overridden @ SP5000 | $469,121.70 | $17,241,771.70 | $281,173,247.58 | $0.00 | $298,884,140.98 | 
Violated & overridden @ SP3000 | $281,473.02 | $10,345,063.02 | $168,703,948.55 | $0.00 | $179,330,484.59 | 
Violated & overridden @ SP2000 | $187,648.68 | $6,896,708.68 | $112,469,299.03 | $0.00 | $119,553,656.39 | 
Violated & overridden @ SP1000 | $93,824.34 | $3,448,354.34 | $56,234,649.52 | $0.00 | $59,776,828.20 | 
Violated & overridden @ SP500 | $46,912.17 | $1,724,177.17 | $28,117,324.76 | $0.00 | $29,888,414.10 | 
Violated & overridden @ SP350 | $32,838.52 | $1,206,924.02 | $19,682,127.33 | $0.00 | $20,921,889.87 | 
Violated & overridden with 2 step limits $200 & $2000 MSP | $18,764.87 | $1,465,179.63 | $97,588,665.34 | $0.00 | $99,072,609.83 | 
Violated & overridden with 2 step limits $200 & $2000 MSP – One constraint at limit + margin with Max Shadow Price at $200 and another at limit with Max Shadow Price at $200 0

## Slide 9: South Load Zone Extra Payment
  Average $/MW for hours when constraint was violated in SCED
  = (7.3 + 43.3)*(1806.83-63.68)=50.6*1743.15
  = $88,203.4
<number>
STLPNT_NAME | AVG(LMP) | Average Load
LZ_SOUTH | $1,806.83 | 6316
LZ_HOUSTON | $58.00 | 11943
LZ_NORTH | $65.44 | 20763
LZ_WEST | $66.68 | 3102
Avg N H W | $63.37 | 11936