| NOGRR Number | 052 | NOGRR Title | Conductor/Transformer Transmission Facility Rating |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | January 13, 2011 |  |  |
| Proposed Effective Date |  | March 1, 2011 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Guide Sections Requiring Revision |  | 3.9.4, Responsibility for Equipment Ratings 9.2.1, Rating Methodology Reporting Program (delete) |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) adds the Conductor/Transformer rating normally used as Rate C in the Annual Planning Models as a fourth Transmission Facility rating required to be provided by Transmission Service Providers (TSPs). |  |  |
| Reason for Revision |  | The Requirement for Conductor/Transformer rating has been required by the Steady State Procedural Manual and is required for compliance with North American Electric Reliability Corporation (NERC) Reliability Standard FAC-010, System Operating Limits Methodology for the Planning Horizon. Additionally, as the other three ratings are included in the Nodal Protocols and Nodal Operating Guides, the fourth rating should be included as well since the Network Model Management System (NMMS) is used for all ratings submissions. |  |  |
| Overall Market Benefit |  | Consistency in Protocol requirements for all Facility Ratings used in NMMS. |  |  |
| Overall Market Impact |  | No impact. |  |  |
| Consumer Impact |  | No impact. |  |  |
| Procedural History |  | - On 9/9/10, NOGRR052 and the associated CEO Revision Request Review and Impact Analysis were posted. - On 10/20/10, the Operations Working Group (OWG) considered NOGRR052. - On 11/17/10, Network Data Support Working Group (NDSWG) comments were posted. - On 11/18/10, OWG again considered NOGRR052. - On 12/15/10, OWG considered the 11/18/10 OWG Report and Impact Analysis for NOGRR052. - On 1/13/11, ROS considered NOGRR052. |  |  |
| OWG Decision |  | On 10/20/10, the OWG was in consensus to table NOGRR052 for one month. On 11/18/10, OWG was in consensus to recommend approval of NOGRR052 as amended by the 11/17/10 NDSWG comments. On 12/15/10, OWG was in consensus to endorse and forward the 11/18/10 OWG Report and the Impact Analysis for NOGRR052 to ROS. |  |  |
| Summary of OWG Discussion |  | On 10/20/10, it was noted that NDSWG requested that OWG table NOGRR052 to allow time for ERCOT and NDSWG to develop comments. On 11/18/10, the NDSWG comments were discussed. On 12/15/10, there was no discussion. |  |  |
| ROS Decision |  | On 1/13/11, ROS unanimously voted to recommend approval of NOGRR052 as recommended by OWG in the 12/15/10 OWG Report. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 1/13/11, there was discussion regarding the Rating definitions in the Protocols and if a conflict would exist with the addition of these terms in the Operating Guides. ERCOT Staff agreed to review the language for potential conflicts and determine if the terms are appropriate in either the Protocols or Operating Guides. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Consistency in Nodal Protocol requirements for all Facility Ratings used in NMMS. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Jay Teixeira |
| E-mail Address | jteixeira@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6582 |
| Cell Number |  |
| Market Segment | N/A |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| NDSWG 111710 | Proposed deleting redundant language regarding submission of rating information and annual report. |

Comments

Please note that updates to Section 3.9.4 have been made due to the November 1, 2010 implementation of NOGRR042, Synchronization of Section 3 with Nodal Protocols.  Revisions are reflected in redline with “NOGRR042” as the author.

Proposed Guide Language Revision

- 3.7.4	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the rating of their facilities and shall send the methodology used to ERCOT  in accordance with paragraph (3) of Protocol Section 3.10, Network Operations Modeling and Telemetry.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide ERCOT with four nominal Transmission Element Ratings:

(a)	Normal Rating:  Represents the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

(b)	Emergency Rating:  Represents the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure.

(c)	15-Minute Rating:  Represents the 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading of 90% of the Normal Rating.  The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading was 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

(d)	Conductor/Transformer Rating:  Represents the two hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The conductor or transformer can operate at this rating for two hours without violation of National Electrical Safety Code (NESC) clearances or equipment failure.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Element to within Normal Ratings as soon as practicable, based on Good Utility Practice.