| NPRR Number | 352 | NPRR Title | Real-Time HSL Telemetry for WGRs |  |
| --- | --- | --- | --- | --- |
| Timeline | Urgent | Action |  | Recommended Approval |
| Date of Decision |  | May 5, 2011 |  |  |
| Proposed Effective Date |  | June 1, 2011 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Protocol Section Requiring Revision |  | 6.5.5.2, Operational Data Requirements |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) changes the process by which Qualified Scheduling Entities (QSEs) determine the High Sustained Limits (HSLs) to telemeter for Wind-powered Generation Resources (WGRs). The requirement that QSEs set the HSL equal to output immediately following a release from curtailment is removed. Instead QSEs will be expected to use their best judgment to determine the output capability of the WGR with the expectation that the value will consider the net real power of the WGR, turbine availability, weather conditions, and whether the WGR output is being affected by compliance with a Security-Constrained Economic Dispatch (SCED) instruction. |  |  |
| Reason for Revision |  | The logic that has been implemented per the current Protocol language has resulted in the underestimation of potential wind power output following a release from curtailment for individual WGRs. This in turn has led to larger than desired control and response oscillations when operating near system transmission limits. The proposed language will create a more clear and consistent view of the real power capabilities of WGRs for ERCOT’s Dispatch systems. |  |  |
| Overall Market Benefit |  | This NPRR will improve reliability of the ERCOT Transmission Grid by allowing ERCOT Dispatch systems to manage congestion appropriately. This NPRR will also improve the efficiency for congestion management and allow for better control when the ERCOT Transmission Grid is operating near the system transfer limits. Additionally, this NPRR should address the unnecessary control of Generation Resources and reduce control and response oscillations observed by ERCOT. |  |  |
| Overall Market Impact |  | The revision will require QSEs representing WGRs to the change the logic process through which they determine the HSL to telemeter to ERCOT in Real-Time for economic Dispatch. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Credit Impacts |  | To be determined. |  |  |
| Procedural History |  | - On 4/13/11, NPRR352 and an Impact Analysis were posted. - On 4/15/11, the motion to grant NPRR352 Urgent status failed via PRS e-mail vote. - On 4/21/11, PRS considered NPRR352. - On 5/5/11, TAC considered NPRR352. |  |  |
| PRS Decision |  | On 4/21/11, PRS unanimously voted to grant NPRR352 Urgent status. PRS then voted to recommend approval of NPRR352 as submitted and to forward NPRR352 to TAC. There was one abstention from the Independent Power Marketer (IPM) Market Segment. All Market Segments were present for the votes. |  |  |
| Summary of PRS Discussion |  | On 4/21/11, ERCOT Staff explained that NPRR352 addresses reliability concerns due to oscillation of the West-to-North transmission constraint, and that this issue was discussed on a WebEx with Market Participants on 4/12/11 and summarized for the ERCOT Board at its 4/19/11 meeting. Participants discussed how the “net output capability” that the QSE for a WGR would be required to telemeter as the WGR’s HSL differs from “Real Time Production Potential (RTPP)” as defined in the zonal Protocols, which would be more volatile. |  |  |
| TAC Decision |  | On 5/5/11, TAC unanimously voted to recommend approval of NPRR352 as recommended by PRS in the 4/21/11 PRS Report. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 5/5/11, concern was expressed that if QSEs submit to ERCOT a WGR’s Real-Time production potential as its output capability it could result in over-deployment of regulation. ERCOT Staff stated that NPRR352 will create a more consistent view of the real power capabilities of WGRs and will improve reliability of the ERCOT Transmission Grid; but agreed to continue to monitor the Real-Time HSL telemetry for WGRs and report the findings to the WMS. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | QSEs representing WGRs will need to change the logic used to determine the HSL being telemetered. | To be determined. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Increased reliability and efficiency in congestion management. | To be determined. |
|  | 2 | Reduction in control signal oscillations for Generation Resources. | To be determined. |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Chad Thompson |
| E-mail Address | cthompson@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6508 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jonathan Levine |
| E-Mail Address | jlevine@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Comments

Please note that the following NPRRs also propose revisions to Section 6.5.5.2:

- NPRR190, Clarification of Resource Definitions and Resource Registration of Self-Serve Generators for Reliability Purposes

- NPRR312, Clarification of QSE Requirements for Split Generation Resources

Proposed Protocol Language Revision

6.5.5.2	Operational Data Requirements

(1)	ERCOT shall use Operating Period data to monitor and control the reliability of the ERCOT Transmission Grid and shall use it in network analysis software to predict the short-term reliability of the ERCOT Transmission Grid.  Each TSP, at its own expense, may obtain that Operating Period data from ERCOT or directly from QSEs.

(2)	A QSE representing a Generation Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time telemetry data to ERCOT for each Generation Resource.  ERCOT shall make that data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to requesting TSPs and DSPs operating within ERCOT.  Such data must be provided to the requesting TSP or DSP at the requesting TSP’s or DSP’s expense, including:

(a)	Net real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered gross real power and conversion constants determined by the Resource Entity and provided to ERCOT as a result of Section 3.7, Resource Parameters.  Net real power represents the actual generation of a Resource for all real power dispatch purposes, including use in Security-Constrained Economic Dispatch (SCED), determination of the High Ancillary Service Limit (HASL), High Dispatch Limit (HDL), Low Dispatch Limit (LDL) and Low Ancillary Service Limit (LASL), and is consistent with telemetered HSL and LSL;

(b)	Gross real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered real power, which may include Supervisory Control and Data Acquisition (SCADA) metering, and conversions constants determined by the Resource Entity and provided to ERCOT as a result of Section 3.7;

(c)	Gross Reactive Power (in Megavolt-Amperes reactive (MVAr));

(d)	Net Reactive Power (in MVAr);

(e)	Power to standby transformers serving plant auxiliary Load;

(f)	Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid;

(g)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(h)	Generation Resource breaker and switch status;

(i)	HSL;

(j)	High Emergency Limit (HEL), under Section 6.5.9.2, Failure of the SCED Process;

(k)	Low Emergency Limit (LEL), under Section 6.5.9.2;

(l)	LSL;

(m)	Configuration identification for Combined Cycle Generation Resources;

(n)	Ancillary Service Schedule for each quantity of RRS and Non-Spin which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment;

(o)	Ancillary Service Resource Responsibility for each quantity of Regulation Up (Reg-Up), Regulation Down (Reg-Down), RRS and Non-Spin.  The sum of Ancillary Service Resource Responsibility for all Resources in a QSE is equal to the Ancillary Service Supply Responsibility for that QSE; and

(p)	Reg-Up and Reg-Down Services participation factors represent how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s).

(3)	For each Wind-powered Generation Resource (WGR), the QSE shall set the HSL equal to the current net output capability of the facility within one SCADA cycle after receiving the last SCED Base Point Dispatch Instruction from ERCOT.  The HSL telemetered to ERCOT for the WGR shall not be changed until the receipt of the next Base Point.  The net output capability should consider the net real power of the WGR, turbine availability, weather conditions, and whether the WGR net output is being affected by compliance with a SCED Dispatch Instruction.  If the Base Point received from ERCOT is less than the telemetered HSL minus two MW, then the WGR shall respond to the Base Point Dispatch Instruction and shall be considered curtailed.  During SCED intervals when the telemetered Base Point of the WGR exceeds the last HSL telemetered to ERCOT minus two MW, the WGR shall be considered as not curtailed.

[NPRR285: Replace paragraph (3) above with the following upon system implementation:] (3) For each Wind-powered Generation Resource (WGR), the QSE shall set the HSL equal to the current net output capability of the facility. The net output capability should consider the net real power of the WGR, turbine availability, weather conditions, and whether the WGR net output is being affected by compliance with a SCED Dispatch Instruction.

(4)	A QSE representing a Load Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Load Resource and ERCOT shall make the data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to the Load Resource’s host TSP or DSP at the TSP’s or DSP’s expense.  The Load Resource’s net real power consumption, Low Power Consumption (LPC) and Maximum Power Consumption (MPC) shall be telemetered to ERCOT using a positive (+) sign convention:

(a)	Load Resource net real power consumption (in MW);

(b)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(c)	Load Resource breaker status;

(d)	LPC (in MW);

(e)	MPC (in MW);

(f)	Ancillary Service Schedule (in MW) for each quantity of RRS and Non-Spin;

(g)	Ancillary Service Resource Responsibility (in MW) for each quantity of Reg-Up and Reg-Down for Controllable Load Resources, and RRS and Non-Spin for all Load Resources;

(h)	The status of the high-set under-frequency relay, if required for qualification;

(i)	For a Controllable Load Resource, the Scheduled Power Consumption that represents zero Ancillary Service deployments;

(j)	For a Controllable Load Resource, net Reactive Power (in MVAr);

(k)	Resource Status (Resource Status shall be ONRL if high-set under-frequency relay is active); and

(l)	Reg-Up and Reg-Down services participation factor, which represents how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource.

(5)	A QSE with Resources used in SCED shall provide communications equipment to receive ERCOT-telemetered control deployments.

(6)	A QSE providing any Regulation Service shall provide telemetry indicating the appropriate status of Resources providing Reg-Up or Reg-Down, including status indicating whether the Resource is temporarily blocked from receiving Reg-Up and/or Reg-Down deployments from the QSE.  This temporary blocking will be indicated by the enabling of the Raise Block Status and/or Lower Block Status telemetry points.

(a)	Raise Block Status and Lower Block Status are telemetry points used in transient unit conditions to communicate to ERCOT that a Resource’s ability to adjust its output has been unexpectedly impaired.

(b)	When one or both of the telemetry points are enabled for a Resource, ERCOT will cease using the regulation capacity assigned to that Resource for Ancillary Service deployment.

(c)	This hiatus of deployment will not excuse the Resource’s obligation to provide the Ancillary Services for which it has been committed.

(d)	These telemetry points shall only be utilized during unforeseen transient unit conditions such as plant equipment failures.  Raise Block Status and Lower Block Status shall only be enabled until the Resource operator has time to update the Resource limits and Ancillary Service telemetry to reflect the problem.

(e)	The Resource limits and Ancillary Service telemetry shall be updated as soon as practicable.  Raise Block Status and Lower Block Status will then be disabled.

(7)	Real-Time data for reliability purposes must be accurate to within three percent.  This telemetry may be provided from relaying accuracy instrumentation transformers.

(8)	Each QSE shall report the current configuration of combined-cycle Resources that it represents to ERCOT.  The telemetered Resource Status for a Combined Cycle Generation Resource may only be assigned a Resource Status of OFFNS if no generation units within that Combined Cycle Generation Resource are On-Line.

(9)	A QSE representing combined-cycle Resources shall provide ERCOT with the possible operating configurations for each power block with accompanying limits.  Combined Cycle Train power augmentation methods may only be included as part of one or more of the registered Combined Cycle Generation Resource configurations.  The Energy Offer Curve in the Three-Part Supply Offer that includes the offered power augmentation method may reflect the price of the added capability.  Such power augmentation methods may include:

(a)	Combustion turbine inlet air cooling (CTIAC) methods;

(b)	Duct firing;

(c)	Other ways of temporarily increasing the output of combined-cycle Resources; and

(d)	For Qualifying Facilities (QFs), an LSL that represents the minimum energy available, in MW, from the Combined Cycle Generation Resource for economic dispatch based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions.