## Slide 1: PDCWG Draft Report to ROS
May 12, 2010
Sydney Niemeyer

## Slide 2: PDCWG Met May 4, 2011
Reviewed disturbance reports.
  Discussed changes in summary reporting to ROS.
Frequency Management presentation by Bob Green.
Frequency control performance, profile and CPS1 review.
  Discussed ERCOT regulation deployment and SCED Base Point oscillations.
  GREDP general review.
Hydro Responsive Reserve and other generator RRS frequency responsive requirements.
  Meeting May 23rd to complete this discussion and form consensus.
NERC BAL-003 field trial and BA requirements for a minimum frequency response requirement with an October 2011 timeline.
NERC manual Time Error Correction field trial to eliminate manual Time Error Corrections is on target to begin this summer.
ERCOT Regional Standard BAL-001-TRE progress update.

## Slide 5
CPS1 12 Month Rolling Average = 149.64
ERCOT CPS1 Score

## Slide 17: Frequency Events Reviewed
Wednesday Mar 16, 2011 @ 20:45
  398 MW -539 MW/0.1 Hz 82% of Bias -103.1 µHz/sec/MWloss
Monday Mar 23, 2011 @ 06:09
  1014 MW -993 MW/0.1 Hz 152% of Bias -97.7 µHz/sec/MWloss
Tuesday Mar 24, 2011 @ 13:59
  569 MW -313 MW/0.1 Hz 48% of Bias -121.3 µHz/sec/MWloss
Friday Mar 25, 2011 @ 16:13
  591 MW -343 MW/0.1 Hz 52% of Bias -86.2 µHz/sec/MWloss
Tuesday Mar 29, 2011 @ 6:43
  735 MW -739 MW/0.1 Hz 113% of Bias -97.9 µHz/sec/MWloss
Thursday Mar 31, 2011 @ 12:21
  420 MW -376 MW/0.1 Hz 58% of Bias -116.6 µHz/sec/MWloss
Tuesday April 5, 2011 @ 22:01
  519 MW -496 MW/0.1 Hz 76% of Bias -150.2 µHz/sec/MWloss
Wednesday April 20, 2011 @ 13:40
  788 MW -545 MW/0.1 Hz 83% of Bias -77.4 µHz/sec/MWloss