TAC Report


	NOGRR Number
	052
	NOGRR Title
	Conductor/Transformer Transmission Facility Rating

	Timeline
	Normal
	Action
	Approved

	Date of Decision
	June 2, 2011

	Effective Date
	July 1, 2011

	Priority and Rank Assigned
	Not applicable

	Guide Sections Requiring Revision
	3.7.4, Responsibility for Equipment Ratings
9.2.1, Rating Methodology Reporting Program (delete)

	Revision Description
	This Nodal Operating Guide Revision Request (NOGRR) adds the Conductor/Transformer rating normally used as Rate C in the Annual Planning Models as a fourth Transmission Facility rating required to be provided by Transmission Service Providers (TSPs).

	Reason for Revision
	The requirement for Conductor/Transformer rating has been required by the Steady State Procedural Manual and is required for compliance with North American Electric Reliability Corporation (NERC) Reliability Standard FAC-010, System Operating Limits Methodology for the Planning Horizon.  Additionally, as the other three ratings are included in the Nodal Protocols and Nodal Operating Guides, the fourth rating should be included as well since the Network Model Management System (NMMS) is used for all ratings submissions.  

	Overall Market Benefit
	Consistency in Protocol requirements for all Facility Ratings used in NMMS.

	Overall Market Impact
	No impact.

	Consumer Impact
	No impact.

	Procedural History
	· On 9/9/10, NOGRR052, the associated CEO Revision Request Review, and Impact Analysis were posted.

· On 10/20/10, the Operations Working Group (OWG) considered NOGRR052.

· On 11/17/10, Network Data Support Working Group (NDSWG) comments were posted.

· On 11/18/10, OWG again considered NOGRR052.

· On 12/15/10, OWG considered the 11/18/10 OWG Report and Impact Analysis for NOGRR052.

· On 1/13/11, ROS considered NOGRR052.

· On 1/24/11, ERCOT comments were posted.

· On 2/3/11, TAC considered NOGRR052.

· On 3/1/11, Oncor comments were posted.

· On 6/2/11, TAC again considered NOGRR052.

	OWG Decision 
	On 10/20/10, the OWG was in consensus to table NOGRR052 for one month.

On 11/18/10, OWG was in consensus to recommend approval of NOGRR052 as amended by the 11/17/10 NDSWG comments. 

On 12/15/10, OWG was in consensus to endorse and forward the 11/18/10 OWG Report and the Impact Analysis for NOGRR052 to ROS.

	Summary of OWG Discussion
	On 10/20/10, it was noted that NDSWG requested that OWG table NOGRR052 to allow time for ERCOT and NDSWG to develop comments.

On 11/18/10, the 11/17/10 NDSWG comments were discussed.

On 12/15/10, there was no discussion.

	ROS Decision
	On 1/13/11, ROS unanimously voted to recommend approval of NOGRR052 as recommended by OWG in the 12/15/10 OWG Report.  All Market Segments were present for the vote.

	Summary of ROS Discussion
	On 1/13/11, there was discussion regarding the Rating definitions in the Protocols and if a conflict would exist with the addition of these terms in the Operating Guides.  ERCOT Staff agreed to review the language for potential conflicts and determine if the terms are appropriate in either the Protocols or Operating Guides.

	TAC Decision
	On 2/3/11, TAC unanimously voted to table NOGRR052.  All Market Segments were present for the vote.

On 6/2/11, TAC unanimously voted to approve NOGRR052 as amended by the 1/24/11 ERCOT comments.  All Market Segments were present for the vote.

	Summary of TAC Discussion
	On 2/3/11, ERCOT Staff requested that NOGRR052 be tabled until the associated NPRR is scheduled for TAC consideration.  The associated NPRR will incorporate language being deleted from the Operating Guides as proposed in NOGRR052 into the Protocols.
On 6/2/11, there was no discussion.


	Quantitative Impacts and Benefits

	Assumptions
	1
	

	
	2
	

	
	3
	

	
	4
	

	Market Cost
	
	Impact Area
	Monetary Impact

	
	1
	None.
	

	
	2
	
	

	
	3
	
	

	
	4
	
	

	Market Benefit
	
	Impact Area
	Monetary Impact

	
	1
	Consistency in Nodal Protocol requirements for all Facility Ratings used in NMMS.
	

	
	2
	
	

	
	3
	
	

	
	4
	
	

	Additional Qualitative Information
	1
	

	
	2
	

	
	3
	

	
	4
	

	Other Comments
	1
	

	
	2
	

	
	3
	

	
	4
	


	Sponsor

	Name
	Jay Teixeira

	E-mail Address
	jteixeira@ercot.com

	Company
	ERCOT

	Phone Number
	(512) 248-6582

	Cell Number
	

	Market Segment
	N/A


	Market Rules Staff Contact

	Name
	Yvette M. Landin

	E-Mail Address
	ylandin@ercot.com

	Phone Number
	(512) 248-4513


	Comments Received

	Comment Author
	Comment Summary

	NDSWG 111710
	Proposed deleting redundant language regarding submission of rating information and annual report.

	ERCOT 012411
	Proposed language changes to remove Transmission Element Ratings definitions from the Operating Guides in an effort to remove potential conflict with the Protocols.

	Oncor 030111
	Proposed changes to the 15-Minute Rating definition. 


	Comments


Please note that the baseline Operating Guide language has been updated in Section 3.7.4 due to the implementation of NOGRR042, Synchronization of Section 3 with Nodal Protocols, into the November 1, 2010 Operating Guides.
Please also note that NOGRR074, Clarified Responsible Entities for Reporting Sabotage Information to NERC, also proposes revisions to Section 3.7.4.
	Proposed Guide Language Revision


3.7.4
Responsibility for Equipment Ratings

(1)
TSPs are responsible for determining the Rating of their Facilities and shall send the methodology used to ERCOT  in accordance with paragraph (3) of Protocol Section 3.10, Network Operations Modeling and Telemetry.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)
TSPs shall provide to ERCOT all nominal Transmission Element Ratings.




(3)
In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:
(a)
ERCOT shall limit pre-contingency flows to enforce the Normal Rating. 

(b)
If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.
(c)
If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)
ERCOT shall use best efforts to restore all Transmission Element to within Normal Ratings as soon as practicable, based on Good Utility Practice.



	




�Please note this Section was revised by NOGRR042, Synchronization of Section 3 with Nodal Protocols.  This Section is also being revised by NOGRR074.





PRR_Template.doc
Page 2 of 1
PRR_Template.doc
Page 2 of 1
052NOGRR-12 TAC Report 060211
Page 4 of 5
PUBLIC

