| NOGRR Number | 069 | NOGRR Title | Relay Misoperation Reporting Changes for Consistency with ERO-RAPA Proposal |
| --- | --- | --- | --- |

| Date | June 1, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Kris Koellner on behalf of the System Protection Working Group (SPWG) |
| E-mail Address | kristian.koellner@lcra.org |
| Company | LCRA |
| Phone Number | (512) 369-4573 |
| Cell Number |  |
| Market Segment | Cooperative |

Comments

These comments revise Section 6.2.3 to address the events that constitute a reportable protective relay system or automatic reclosing misoperation.  Specifically item (e) was renumbered to paragraph (3) as it is not such an event.  Paragraph (3) clarifies events that are not categorized as misoperations. These comments also include ERCOT as the recipient of the quarterly data submittal in order to allow ROS working groups to have access to the reported data for review as needed.

Revised Proposed Cover Page Revision

- 6.2.1	Introduction

(1)	The satisfactory operation of the ERCOT System (equipment operated above 60 kV), especially under abnormal conditions, is greatly influenced by protective relay systems.  Protective relay systems are defined as the total combination of:

(a)	The protective relays;

(b)	Associated communications system;

(c)	Voltage and current sensing devices; and

(d)	The station DC supply associated with protective functions (including batteries, battery chargers, and control circuitry).

- (2)	Although relaying of tie points between facility owners is of primary concern to the ERCOT System, internal protective relay systems often directly, or indirectly, affects the adjacent area also.  Facility owners are those Entities owning facilities in the ERCOT System.  Facility owners have an obligation to implement relay application, operation, and preventive maintenance criteria that assure the highest practicable reliability and availability of service to the ultimate power consumers of the concerned area and neighboring areas.  Protective relay systems of individual facility owners shall not adversely affect the stability of ERCOT System interconnections.  Additional minimum protective relay system requirements are outlined in the North American Electric Reliability Corporation (NERC) Reliability Standards.

- 6.2.3	Performance Analysis Requirements for ERCOT System Facilities

(1)	All ERCOT System disturbances (unwanted trips, faults, and protective relay system operations and automatic reclosing operations) shall be analyzed by the affected Facility owner(s) promptly and any deficiencies shall be investigated and corrected.

(2)	All protective relay system and automatic reclosing misoperations in Resource systems and Transmission Facility systems 100 kV and above shall be documented, including corrective actions and the documentation supplied by the affected Facility owner(s) to ERCOT or NERC upon their request within five Business Days.  All protective relay system and automatic reclosing misoperations shall be documented quarterly using the format in Section 8, Attachment B, Protection System Misoperation Report.  Any of the following events constitute a reportable protective relay system or automatic reclosing misoperation:

(a)	Failure to Trip – Any failure of a protective relay system to initiate a trip to the appropriate terminal when a fault is within the intended zone of protection of the device (zone of protection includes both the reach and time characteristics);

(b)	Slow Trip – A correct operation of a protective relay system for a fault in the intended zone of protection where the relay system initiates tripping slower than the system design intends;

(c)	Unnecessary Trip During a Fault – Any initiated operation of a circuit breaker during a fault when the fault is outside the intended zone of protection; and

(d)	Unnecessary Trip Other Than Fault – The unintentional operation of a protective relay system, which causes a circuit breaker to trip when no system fault is present.  May be due to vibration, improper settings; load swing, defective relays, or SCADA system malfunction;

(e)	Failure to Reclose – Any failure of a protective relay system or automatic reclosing to automatically reclose following a fault if that is the system design intent.

(3)	Facility owner authorized personnel action that directly initiates a trip is not included in this category.  It is the intent of this reporting process to identify misoperations of the protective relay system as it interrelates with the electrical system, not as it interrelates to personnel involved with the protective relay system.  If an individual directly initiates an operation, it is not counted as a misoperation (i.e., unintentional operation during tests); however, if a technician leaves trip test switches or cut-off switches in an inappropriate position and a system fault or condition causes a misoperation, this would be counted as a protective relay system misoperation.

(4)	All SPS misoperations shall be documented, including corrective actions and the documentation supplied to ERCOT and NERC upon request within five Business Days.  SPS misoperations shall be included in the quarterly misoperations report requirements.  All SPS misoperations shall be documented using the format in Section 8, Attachment B.  Any of the following events constitute a reportable SPS misoperation:

(a)	Failure to Operate – Any failure of a SPS to perform its intended function within the designed time when system conditions intended to trigger the SPS occur;

(b)	Failure to Arm – Any failure of a SPS to automatically arm itself for system conditions that are intended to result in the SPS being automatically armed;

(c)	Unnecessary Operation – Any operation of a SPS that occurs without the occurrence of the intended system trigger condition(s);

(d)	Unnecessary Arming – Any automatic arming of a SPS that occurs without the occurrence of the intended arming system condition(s); and

(e)	Failure to Reset – Any failure of a SPS to automatically reset following a return of normal system conditions if that is the system design intent.

(5)	Facility owners shall document the performance of their protective relay systems utilizing the method described in the paper “Transmission Protective Relay System Performance Measuring Methodology,” IEEE/PSRC Working Group I3 September 16, 1999.  The performance data reported shall include the total number of protective relay system and automatic reclosing misoperations, the total number of events, and the factor “k.”

(6)	Reporting of protective relay system and automatic reclosing misoperations shall be submitted to the Texas Reliability Entity (TRE) and ERCOT on a quarterly basis per the following schedule:

| Data submission | Date |
| --- | --- |
| Submission of the 1st Quarter data | May 31 |
| Submission of the 2nd Quarter data | August 31 |
| Submission of the 3rd Quarter data | November 30 |
| Submission of the 4th Quarter data and IEEE Protective Relay System Performance summary | February 28 |

(7)	At least annually, ROS designated working groups shall review the protective relay system and automatic reclosing misoperation reports and, at least annually, 345 kV performance data of Facility owners for analysis of protective relay system and automatic reclosing performance.

(8)	All Facility owners shall install, maintain, and operate disturbance monitoring equipment in accordance with the requirements in Section 6.1.2.3, Data Recording Requirements.

(9)	Facility owners shall provide an assessment of the system performance results of simulation tests of the contingencies as required by NERC Reliability Standards.  These assessments should be based on existing protection systems and any existing backup or redundancy protection systems to determine that existing transmission protection systems are sufficient to meet the system performance levels as defined in NERC Reliability Standards.  All non-compliance findings shall be documented per NERC requirements, including a plan for achieving compliance.  These assessments shall be provided to NERC or ERCOT upon their request within 30 days of the request.

Section 8, Attachment B, Protection System Misoperation Report

- Protection System Misoperation Report

Protective relay system and automatic reclosing misoperations shall be reported in the format requested by the Texas Reliability Entity (TRE).  As a minimum, all fields of data specified in the table below shall be included in the report.  The file shall include the "Field Names" listed in the table below as headers for each field and the data size/format shall match "Size and/or Format" specified in the table below.

Each row in the Protection System Misoperation Report records one misoperation. If an event has more than one misoperation associated with it, there should be more than one row reported that pertains to the event. In a multi-misoperation event, information from one misoperation can be copied or repeated in another misoperation associated with the same event, if appropriate. In this case, providing the Transmission Availability Data System (TADS) event code identifies that each misoperation was associated with a single event.

| Field Name | Type | Size and/or Format | Description |
| --- | --- | --- | --- |
| - Resubmittal Check | Text | Drop down | NERC reporting requirements include quarterly reporting. Individual misoperation entries may require review and updates that bridge the quarterly reporting requirements. To capture metrics properly notification of resubmittal is required. Default is No. |
| - Regional Entity | Text | Drop down | Name of Regional Entity |
| - Entity Name | Text | 25 characters | Name of Entity (NERC Registration Name) |
| - Misoperation Date | Date | mm/dd/yyyy | The date of the misoperation. |
| - Misoperation Time | Time | hh:mm:ss | The time at which misoperation occurred in 24-hour format – this could be time marked by the relay if it is synchronized with GPS clock, time noted by each facility owner’s or operator’s operations control center. |
| - Time zone | Text | Drop down | Define the standard time zone of the misoperation time noted (i.e. CST, EST, etc.) |
| - Facility Name (Location of misoperation) | Text | Name used in Network Operations Model per TAC approved naming convention | Identify the name of the facility (i.e., substation or generating station) where the misoperation occurred. |
| - Equipment Name (protected by Protection System that Misoperated) | Text | Name used in Network Operations Model per TAC approved naming convention | Identify by name the generator, transmission line, transformer, bus or equipment protected by the Protection System that Misoperated. |
| - Equipment Type | Text | Drop down | Select type of equipment being protected ( e.g., Line, Transformer, etc.) from drop-down list |
| - Facility Voltage | Text | Drop down | Select system voltage (in kV) of the protected element (if transformer, high side kV) from drop-down list. |
| - Equipment Removed from Service | Text | 32,767, utilizing Names used in Network Operations Model per TAC approved naming convention | Enter names of the equipment becoming unavailable due to the event (Equipment only refers to circuits, transformers, busses, but not breakers UNLESS the breaker is the only element). |
| - Event Description | Text | 32,767 | Provide a brief description of the event and detailed description of misoperation root causes (see cause code in Column N). |
| - Misoperation Category | Text | Drop down | Select Misoperation Category from drop-down list. |
| - Cause(s) of misoperation | Text | Drop down | Select root cause(s) of the misoperation from drop-down list. Detailed definitions of the root causes are provided. |
| - Protection Systems/Components that Misoperated | Text | 32,767 | Only provide information on the components/protective relay systems that misoperated. If misoperated components are relays, list relay models (types) and protection schemes. |
| - Relay Technology | Text | Drop down | Select Electromechanical, Solid State, or Micro Processor from drop-down list |
| - Is this a TADS reportable outage? | Text | Automated | This field is automatically populated based on Voltage selection. No manual entry is needed. |
| - Corresponding TADS Cause Code | Text | Automated | This field is automatically populated to show the corresponding TADS cause code(s). No manual entry is needed. |
| - Enter one or more TADS "Event IDs" if this is a TADS reportable outage? | Text | 32,767 | Create a TADS Event ID using TADS Form 5 |
| - Analysis and Corrective Action Status | Text | Drop down | Select the status from drop-down list. In general, misoperation analysis is conducted first, and then a Corrective Action Plan will be developed and implemented to mitigate the misoperation. |
| - Corrective Action Plan | Text | 32,767 | Identify the corrective action(s). |
| - Corrective Action Plan Target Completion Date | Date | mm/dd/yyyy | If corrective actions are not complete, estimate when they will be complete. |
| - Actual Completion Date | Date | mm/dd/yyyy | If corrective actions are complete, enter actual completion date. |
| - Reported By | Text | 25 | Enter the name of the person filling out the report. |
| - Phone | Text | 50 | Enter the reporting person’s phone number. |
| - E-Mail | Text | 50 | Enter the reporting person’s E-MAIL address. |
| - Date Reported | Date | mm/dd/yyyy | Enter the report date. |

| Causes(s) of Misoperation |  |
| --- | --- |
| AC system | This category includes misoperations due to problems in the ac inputs to the protective relay system. Examples would include misoperations associated with CT saturation, loss of potential, or rodent damaged wiring in voltage or current circuit. |
| As-left personnel error | This category includes misoperations due to the as-left condition of the protective relay system following maintenance or construction procedures. These include test switches left open, wiring errors not associated with incorrect drawings, carrier grounds left in place, or settings placed in the wrong relay, or incorrect field settings left in the relay that do not match engineering approved settings. |
| Communication failures | This category includes misoperations due to failures in the communication systems associated with protection schemes inclusive of transmitters and receivers. Examples would include misoperations caused by loss of carrier, spurious transfer trips associated with noise, Telco errors resulting in malperformance of communications over leased lines, loss of fiber optic communication equipment, or microwave problems associated with weather conditions. |
| DC system | This category includes misoperations due to problems in the DC control circuits. These include problems in the battery or charging systems, trip wiring to breakers, or loss of dc power to a relay or communication device. |
| Incorrect setting/logic/design errors | This category includes misoperations due to “engineering” errors by the protective relay system owner. These include setting errors, errors in documentation, and errors in application. Examples would include uncoordinated settings, incorrect schematics, or multiple CT grounds in the design. |
| Relay failures/malfunctions | This category includes misoperations due to improper operation of the relays themselves. These may be due to component failures, physical damage to a device, firmware problems, or manufacturer errors. Examples would include misoperations caused by changes in relay characteristic due to capacitor aging, misfiring thyristors, damage due to water from a leaking roof, relay power supply failure, or internal wiring/logic error. Failures of auxiliary tripping relays fall under this category. |
| Unknown/unexplainable | Requires extensive documentation of investigative actions if this cause code is utilized. |