| NOGRR Number | 074 | NOGRR Title | Clarified Responsibly Entities for Reporting Sabotage Information to NERC |
| --- | --- | --- | --- |
| Date |  | June 14, 2011 |  |
| Submitter’s Information |  |  |  |
| Name |  | DeAnn Walker |  |
| E-mail Address |  | deann.walker@CenterPointEnergy.com |  |
| Company |  | CenterPoint Energy |  |
| Phone Number |  | 512-397-3032 |  |
| Cell Number |  | 512-784-0998 |  |
| Market Segment |  | IOU |  |

Comments

CenterPoint Energy does not believe there is a need for the proposed change.  The language being deleted in Subsection 3.7.3 is very similar to the new proposed language in Subsection 3.8.  In fact, although the words have been modified, there are no significant changes in the requirements that are necessary, except for the inclusion of the last sentence.  Therefore, CenterPoint Energy believes the changes are unnecessary and should be rejected.

In the event that the changes are not rejected, the last sentence in the new Subsection 8 should be deleted.  It states that the North American Electric Reliability Corporation (NERC) Register Entities are required to comply with the NERC Standards.  There are already Federal laws that require such compliance; therefore, it is unnecessary to include such a provision in the Operating Guides.

Revised Proposed Guide Language

3.7.3	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the rating of their facilities.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide ERCOT with three nominal Transmission Element Ratings:

(a)	Normal Rating:  Represents the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

(b)	Emergency Rating:  Represents the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure.

(c)	15-Minute Rating:  Represents the 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading of 90% of the Normal Rating.  The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading was 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Elements to within Normal Ratings as soon as practicable, based on Good Utility Practice.

- 3.8	Requirements for Reporting Sabotage Information

Any Entity registered with North American Electric Reliability Corporation (NERC) or ERCOT-registered Entity (Resource Entity, Transmission and/or Distribution Provider (TDSP)) or its Designated Agent (Qualified Scheduling Entity (QSE), Transmission Operator (TO)) shall report to ERCOT at shiftsupervisors@ercot.com when disturbances or unusual occurrences are suspected or determined to be caused by sabotage and shall have procedures for the recognition of sabotage events at its facilities.