| PGRR Number | 005 | PGRR Title | New Planning Guide Section 5, Planning Criteria |
| --- | --- | --- | --- |

| Date | May 20, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-mail Address | ylandin@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-4513 |
| Cell Number |  |
| Market Segment | N/A |

Comments

ERCOT submits these comments to rename the title of Planning Guide Revision Request (PGRR) 005 to accurately reflect the new Section of the Planning Guide being developed by PGRR005.   These comments also propose non-substantive administrative changes to the following Sections:

- 2.1

- 4.1

- 4.2.1.1

- 4.2.1.2

- 4.3.1

Revised Cover Page Language

| PGRR Number | 005 | PGRR Title | New Planning Guide Section 4, Planning Criteria |
| --- | --- | --- | --- |

Revised Proposed Guide Language

2.1	Definitions

Credible Single Contingency for Transmission Planning (for operations planning purposes Credible Single Contingency is defined in the Operating Guides):

(1)	A single facility, comprised of transmission line, auto transformer, or other associated pieces of equipment.  This includes multiple equipment Outaged or interrupted during a single fault (SFME).

(2)	The Forced Outage of a DCKT in excess of 0.5 miles in length (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause the following:

(a) 	Cascading or uncontrolled Outages;

(b) 	Instability of Generation Resources at multiple plant locations; or

(c) 	Interruption of service to firm demand or generation other than that isolated by the transmission facility, following the execution of all automatic operating actions such as relaying and Special Protection Systems (SPSs).

Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans (RAPs)) such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage or thermal ratings being exceeded.

(3)	Any Generation Resource:

(a)	A combined-cycle facility shall be considered a single Generation Resource; or.

(b)	Each unit of a combined-cycle facility will be considered a single Generation Resource if the combustion turbine and the steam turbine can operate separately, as stated in the Resource registration on the Market Information System (MIS) Public Area.

(4)	With any single Generation Resource unavailable, and with any other generation preemptively redispatched, the contingency loss of a single Transmission Facility (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause the following:

(a) 	Cascading or uncontrolled Outages;

(b) 	Instability of Generation Resources at multiple plant locations; or

(c) 	Interruption of service to firm Demand or generation other than that isolated by the Transmission Facility, following the execution of all automatic operating actions such as relaying and SPSs.

(5)	Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., RAPs) such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage or thermal ratings being exceeded.

(6) 	Single contingency conditions defined in North American Electric Reliability Corporation (NERC) Reliability Standards and any subsequent revisions.

ERCOT Planning Guide

Section 4:  Transmission Planning Criteria

month, xx, yyyy

4	TRANSMISSION PLANNING CRITERIA	5

4.1	Introduction	5

4.2	Reliability Criteria	6

4.3	ERCOT Application of NERC Standards for System Assessments	7

4.3.1	Category C	7

4.3.2	Category D	8

# tRANSMISSION pLANNING CRITERIA

- 4.1	Introduction

(1)	ERCOT employs both reliability criteria and economic criteria in evaluating the need for transmission system improvements.  The economic criteria are included in Protocol Section 3.11.2, Planning Criteria, and this Planning Guide provides the reliability criteria.

(2)	The ERCOT System consists of those generation and Transmission Facilities (60 kV and higher voltages) that are controlled by individual Market Participants and that function as part of an integrated and coordinated system.  Each reference in this document to Market Participants includes Generation Resources, Qualified Scheduling Entities (QSEs), Competitive Retailers (CRs), Transmission Service Providers (TSPs), Distribution Service Providers (DSPs) and others that use the ERCOT Transmission Grid.

(3)	To maintain reliable operation of the ERCOT System, it is necessary that all stakeholders observe and subscribe to certain minimum planning criteria.  The criteria set forth herein, combined with the applicable North American Electric Reliability Corporation (NERC) Reliability Standards, constitute the aforementioned minimum planning criteria.  Tests outlined herein shall be performed to determine conformance to these minimum criteria; however, ERCOT recognizes that events more severe than those outlined in these criteria could cause grid separation and other tests may also be performed.

(4)	The complexity and uncertainty inherent in the planning and operation of the ERCOT System make exhaustive studies impracticable; therefore, to gain maximum benefit from the limited number of tests performed, the selection of the specific tests and the frequency of their performance will be made solely upon the basis of the expected value of the reliability information obtainable from the test.

(5)	It is the responsibility of each TSP to perform steady state, short circuit and dynamic tests appropriate to ensure the reliability of its Transmission Facilities and implement appropriate solutions.  Further the TSP may recommend additional studies be performed by ERCOT or through the Reliability and Operations Subcommittee (ROS).  Additional tests which may affect multiple TSPs or the ERCOT System as a whole may be studied.  Upon consideration of such recommendations, ERCOT and the ROS shall coordinate the performance of such studies, as necessary, to assess the reliability of the planned ERCOT System.

(6)	The Regional Planning Group (RPG) or ERCOT shall determine and demonstrate the need for any static and/or dynamic Reactive Power capability in excess of the explicit requirements of the Protocols and Operating Guides that is necessary to ensure compliance with the planning criteria.  ERCOT shall establish specific TSP responsibility for any associated facility additions.

(7)	The base cases created by the Steady State Working Group (SSWG), Dynamics Working Group (DWG), System Protection Working Group (SPWG), and ERCOT are available for use by Market Participants.

(8)	If a TSP has its own planning criteria in addition to those defined in this Guide, the TSP shall provide documentation of those criteria to ERCOT.  ERCOT shall post the documentation on the Planning and Operations Information website.  The TSP shall notify ERCOT of any changes to their planning criteria and provide revised documentation within 30 days of such change.

- 4.2	Reliability Criteria

- 4.2.1	Planning Assumptions

The contingency studies will be performed for reasonable variations of Load level, generation schedules, planned transmission line Maintenance Outages, and anticipated power transfers.  At a minimum, this should include projected Loads for the upcoming summer and winter seasons (seasons as defined in subsection 2.1.2, Data Set A Case Definitions, of Section 9, Appendices, A, Steady State Working Group Procedures Manual, and a five-year planning horizon.  The Transmission Service Providers (TSPs) involved should plan to resolve any unacceptable study results through the provision of Transmission Facilities, the temporary alteration of operating procedures (i.e., Remedial Action Plans (RAPs)), temporary Special Protection Systems (SPSs), or other means as appropriate.

- 4.2.1.1	Performance Requirements for Credible Single Contingencies

Credible Single Contingencies for Transmission Planning as defined in Section 2.1, Definitions, of this Planning Guide, shall not result in the following:

(a)	Cascading or uncontrolled Outages;

(b)	 Instability of generating units at multiple plant locations; or

(c)	Interruption of service to firm demand or generation other than that isolated by the double-circuit loss, following the execution of all automatic operating actions such as relaying and SPSs.  Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., RAPs), such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage limits or thermal ratings associated with the Transmission Facility being exceeded.

- 4.2.1.2	Voltage Stability Margin

Voltage stability margin shall be sufficient to maintain post-transient voltage stability   under the following study conditions for each ERCOT or TSP-defined areas:

(a)	A 5% increase in Load above expected peak supplied from resources external to the ERCOT or TSP-defined areas; and North American Electric Reliability Corporation (NERC) Category A or B operating conditions; and

(b)	A 2.5% increase in Load above expected peak supplied from resources external to the ERCOT or TSP-defined areas and NERC Category C operating conditions.

### 4.3	ERCOT Application of NERC Standards for System Assessments

#### 4.3.1	Category C

(1)	Bus Section Definition - "Bus Section" shall be interpreted to mean any section of buswork, which would be isolated by normal relay/breaker operation when faulted.

(2)	Manual System Adjustments Definition - "Manual System Adjustments" shall be interpreted to include only operator actions that:

(a)	Would be made no later than one hour after clearing of the first fault;

(b)	Are made using remote control capability or communications with other operators having such capability;

(c)	Include circuit switching, changes in the schedules of generating units operating at clearing of the first fault, and changes in the schedules of other generating units that can contribute within one hour; and

(d)	Exclude the physical repair or replacement of damaged equipment and the starting of any generating unit that cannot contribute within one hour.

(3)	Planned Loss of Demand or Curtailed Firm Transfer Definition - All Load interruption, generator tripping, or generation schedule changes must be either automatic or prearranged with associated written operating procedures.  Actions must be executable in time to avoid any equipment damage or safety violations, but in any case within 30 minutes of fault clearing.

(4)	Cascading Outage Definition - Cascading Outages are defined as the uncontrolled loss of any system facilities or load, whether because of thermal overload, voltage collapse, or loss of synchronism, except those occurring as a result of fault isolation.

(5)	Implementation Guidelines - Evaluation of all the possible combination of facility Outages under Category C is not required.  Each Transmission Service Provider (TSP) with bulk Transmission Facilities will evaluate one or more Category C contingencies annually.  The contingencies selected may be based on the results of related studies or actual events.  In either case, the selected contingencies must indicate more severe results or impacts based on the engineering judgment of the facility owner, ERCOT or any TSP.  An explanation of why any remaining contingencies would produce less severe system results shall be available as supporting information.

#### 4.3.2	Category D

(1)	For the purpose of evaluating the consequences resulting from a Category D event, a Large Load or Major Load Center is an electrical demand of between 50 and 500 MW.  This may be a large single Load or a group of electrically close Loads.  The loss of this demand will not include any other system elements other than those directly connected.

(2)	Evaluations of Category D contingencies are not required to be performed annually.  Evaluations should be performed for the following:

(a)	Contingencies previously studied for which the conditions assumed in the study have changed significantly and which may adversely affect the results of the study; and

(b)	Contingencies not previously studied that, based on the results of related studies or actual events may in the engineering judgment of the facility owner, ERCOT or any TSP, have unacceptable consequences.