| NOGRR Number | 068 | NOGRR Title | Hydro-Responsive Reserve |  |
| --- | --- | --- | --- | --- |
| Timeline | Urgent | Action |  | Recommended Approval |
| Date of Decision |  | June 16, 2011 |  |  |
| Proposed Effective Date |  | Upon TAC approval. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Guide Section Requiring Revision |  | 2.3.1.2, Additional Operational Details for Responsive Reserve Providers |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) adds a frequency requirement for the deployment of synchronous condenser fast response service to the Nodal Operating Guides. |  |  |
| Reason for Revision |  | The frequency requirement existed in zonal Operating Guide Section 2.5.2.3, Types of Responsive Reserve, but was inadvertently omitted from the Nodal Operating Guides |  |  |
| Overall Market Benefit |  | Assists in maintaining reliability of the ERCOT System by making this service available more quickly and preventing frequency from dropping further. |  |  |
| Overall Market Impact |  | Reliability of the ERCOT System. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Procedural History |  | - On 3/31/11, NOGRR068 and an Impact Analysis were posted. - On 4/1/11, the motion to grant NOGRR068 Urgent status failed via ROS e-mail vote. - On 4/11/11, ROS considered NOGRR068. - On 5/10/11, Performance Disturbance Compliance Working Group comments were posted (PDCWG). - On 5/12/11, ROS again considered NOGRR068. - On 6/7/11, a second set of PDCWG comments were posted. - On 6/16/11, ROS again considered NOGRR068. |  |  |
| ROS Decision |  | On 4/11/11, ROS voted to grant NOGRR068 Urgent status via roll-call vote. ROS then unanimously voted to table NOGRR068. All Market Segments were present for the votes. On 5/12/11, ROS unanimously voted to table NOGRR068 for one month. All Market Segments were present for the vote. On 6/16/11, ROS unanimously voted to recommend approval of NOGRR068 as submitted with a proposed effective date “of upon TAC approval” and to forward NOGRR068 and the Impact Analysis to TAC. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 4/11/11, the need for Urgent status was debated. ERCOT Staff stated that Urgent status is needed to ensure reliability of the ERCOT System during high Demand periods and that this NOGRR aligns the Nodal Operating Guides with language that existed in the zonal Operating Guides. There was concern expressed regarding the treatment of hydro in the Nodal Market. It was noted that a holistic review of Responsive Reserve (RRS) is needed. There was a request for the PDCWG to review the reliability aspects of NOGRR068. On 5/12/11, it was noted that the PDCWG requested additional time to review NOGRR068. On 6/16/11, ERCOT Staff stated that comments were forthcoming to further clarify the requirements of hydro-powered Resources and compliance concerns expressed by LCRA. ROS discussed the urgency to implement NOGRR068 and agreed that it should be effective upon TAC approval. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Unknown | Unknown |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Assists in maintaining reliability of the ERCOT System by making this service available quicker and preventing frequency from dropping further. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | No impacts to ERCOT systems. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Isabel Flores |
| E-mail Address | iflores@ercot.com |
| Company | ERCOT |
| Phone Number | 512/248-6531 |
| Cell Number | 512/565-9117 |
| Market Segment | N/A |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | 512/248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| PDCWG 051211 | Requested time to further review NOGRR068 to better understand the effect certain market design changes in Nodal have on Primary Frequency Response and to provide ROS with observations and recommendations as appropriate. |
| PDCWG 060711 | Opined on frequency relay setting of 59.750 Hz vs. 59.900 Hz and its effect on reliability. |

Proposed Guide Language Revision

- 2.3.1.2	Additional Operational Details for Responsive Reserve Providers

(1)	ERCOT shall specify the minimum amount of RRS provided by Generation Resources.  QSE’s Generation Resources providing RRS must be On-Line and capable of ramping to the awarded output level within ten minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.

(2)	RRS provided by a QSE shall meet the requirements as defined in item (3) of Protocol Section 3.18, Resource Limits in Providing Ancillary Service.

(3)	Load Resources providing RRS must be controlled by under-frequency relays for automatic interruption.  For eligibility to participate as a RRS provider, reference Protocol Section 8.1.1.2.1.2, Responsive Reserve Service Qualification.  Load Resources shall also complete the following requirements:

(a)	The under-frequency relay must have a delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles).  Total time from the time frequency first decays to a value low enough to initiate action of the under frequency relay(s) to the time Load is interrupted should be no more than 30 cycles, including all relay and breaker operating times;

(b)	The initiation setting of the under-frequency relay shall not be any lower than 59.7 Hz; and

(c)	Load Resource must be able to remain interrupted during actual event until replaced by other net dependable capability.  In no case may interrupted Load be restored to service without the approval of an ERCOT operator.

(4)	To become and remain fully qualified as a provider of RRS, the Load shall complete the requirements above and the following:

(a)	Pass simulated or actual testing according to ERCOT procedures; and,

(b)	Perform verification testing as described in Section 8, Attachment G, Load Resource Tests.

(5)	A Direct Current Tie (DC Tie) may be used as RRS up to 30 MW subject to the following constraints:

(a)	The tie shall respond with increased deliveries to ERCOT or decreased deliveries from ERCOT at a frequency of 59.9 Hz;

(b)	The response rate will not be less than 30 MW per minute;

(c)	The response delay will not exceed four seconds;

(d)	The response will be retained until frequency has recovered to a level at or above 60.00 Hz or as directed by ERCOT;

(e)	A QSE claiming DC Tie RRS must demonstrate the existence of contracts agreeing to provide the required response with the DC Tie operator; and

(f)	A QSE claiming DC Tie RRS must have an agreement with the balancing authority on the opposite side of the DC Tie involved approving the amount and conditions.

(6)	Hydro Unit(s) – Modes of RRS that will be counted:

(a)	Synchronous condenser fast response mode - described in item (3) of Protocol Section 3.18 and with automatic controls using the fast-response mode in operation to initiate a move to the generating mode.  The initiation setting of the automatic controls shall not be lower than 59.9 Hz and the Generation Resource must be generating within four seconds of the set relay operation;

(b)	Generation MW mode - For any hydro powered resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 20% of the High Sustained Limit (HSL);

(c)	Synchronous Condenser Mode in “Manual” Dispatch Mode - Units will supply MWs based on operator action within the ten-minute Protocol requirement for supplying RRS.  Once deployed these units are frequency responsive; and

(d)	A Real-Time signal of the MW capacity of hydro units being operated in any of the synchronous condenser modes is telemetered to ERCOT.