| NPRR Number | 362 | NPRR Title | Changes to PRC Calculation |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | July 7, 2011 |  |  |
| Proposed Effective Date |  | September 1, 2011 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Protocol Sections Requiring Revision |  | 6.5.7.5, Ancillary Services Capacity Monitor 6.5.9.4.2, EEA Levels |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) aligns the Protocols with the current systems. The proposed changes properly reflect the current Responsive Reserve (RRS) which is supplied from Load Resources into the Physical Responsive Capability (PRC) calculation. This NPRR also deletes the method for calculating the PRC from Energy Emergency Alert (EEA) Levels 1 and 2. |  |  |
| Reason for Revision |  | Protocol language could be interpreted to require a higher PRC than that determined by current systems. |  |  |
| Overall Market Benefit |  | Clarification of PRC requirement. |  |  |
| Overall Market Impact |  | Clarification of PRC requirement. |  |  |
| Consumer Impact |  | Clarification of PRC requirement. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR362 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 5/4/11, NPRR362 and the associated Impact Analysis were posted. - On 5/19/11, PRS considered NPRR362. - On 6/23/11, PRS considered the 5/19/11 PRS Report and Impact Analysis for NPRR362. - On 6/29/11, ERCOT Comments were posted. - On 7/7/11, TAC considered NPRR362. |  |  |
| PRS Decision |  | On 5/19/11, PRS voted to recommend approval of NPRR362 as revised by PRS. There was one abstention from the Independent Generator Market Segment. All Market Segments were present for the vote. On 6/23/11, PRS unanimously voted to endorse and forward the 5/19/11 PRS Report and Impact Analysis for NPRR362 to TAC. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 5/19/11, there was no discussion. On 6/23/11, there was no discussion. |  |  |
| TAC Decision |  | On 7/7/11, TAC unanimously voted to recommend approval of NPRR362 as amended by the 6/29/11 ERCOT comments. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 7/7/11, the 6/29/11 ERCOT comments were discussed. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Clarification of PRC requirement. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Isabel Flores |
| E-mail Address | iflores@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6531 |
| Cell Number | 512-565-9117 |
| Market Segment | N/A |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 062911 | Incorporated NPRR362 proposed language into the gray-box in Section 6.5.7.5. |

Comments

Please note that the baseline Nodal Protocol language in Section 6.5.7.5 has been updated due to the recent incorporation NPRR350, Change to the Security Classification of the System Ancillary Service Capacity Monitor Dashboard, into the Nodal Protocols on June 1, 2011.

Please also note that the following NPRRs also propose revisions to the following Sections:

- Section 6.5.7.5:

  - NPRR378, Posting of the ERCOT Short-Term Load  Forecast and the Aggregated HDL and LDL Used in SCED

- Section 6.5.9.4.2:

- NPRR356, EEA Changes Related to Dispatch Instructions and BLTs

- NPRR379, EILS Dispatch Sequence and Performance Criteria Upgrades

Proposed Protocol Language Revision

- 6.5.7.5	Ancillary Services Capacity Monitor

(1)	ERCOT shall calculate the following every ten seconds and provide Real-Time summaries to ERCOT Operators and all Market Participants using ICCP, giving updates of calculations every ten seconds, and posting on the MIS Secure Area, giving updates of calculations every five minutes, which show the Real-Time total system amount of:

(a)	RRS capacity from Generation Resources;

(b)	RRS capacity from Load Resources excluding Controllable Load Resources;

(c)	RRS capacity from Controllable Load Resources;

(d)	Non-Spin available from On-Line Generation Resources with Energy Offer Curves;

(e)	Non-Spin available from undeployed Load Resources;

(f)	Non-Spin available from Off-Line Generation Resources;

(g)	Non-Spin available from Resources with Output Schedules;

(h)	Undeployed Reg-Up and undeployed Reg-Down;

(i)	Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED;

(j)	Available capacity with Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED;

(k)	Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED;

(l)	Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED; and

(m)	The ERCOT-wide Physical Responsive Capability (PRC) calculated as follows:

generationresourcei=onlineonlinegenerationAllresources

PRC1 =			Min(Max((RDF*HSL – Actual Net Telemetered Output)i , 0.0) , 0.2*RDF*HSLi)

generationresourcei=onlineonlinegenerationAllresources

PRC2 =	((Hydro-synchronous condenser output)i as qualified by item (6) of Operating Guide Section 2.3.1.2, Additional Operational Details for Responsive Reserve Providers))





resources

load

online

All

resource

load

online

i

PRC3 =			(RRS MW supplied from Load Resources)i

PRC =	PRC1 + PRC2 + PRC3

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PRC1 | MW | Generation On-Line greater than 0 MW |
| PRC2 | MW | Hydro-synchronous condenser output |
| PRC3 | MW | RRS supplied from Load Resources |
| PRC | MW | Physical Responsive Capability |
| RDF |  | The currently approved Reserve Discount Factor |

[NPRR350: Replace paragraph (1) above with the following upon system implementation:] (1) ERCOT shall calculate the following every ten seconds and provide Real-Time summaries to ERCOT Operators and all Market Participants using ICCP, giving updates of calculations every ten seconds, and posting on the MIS Public Area, giving updates of calculations every five minutes, which show the Real-Time total system amount of: (a) RRS capacity from Generation Resources; (b) RRS capacity from Load Resources excluding Controllable Load Resources; (c) RRS capacity from Controllable Load Resources; (d) Non-Spin available from On-Line Generation Resources with Energy Offer Curves; (e) Non-Spin available from undeployed Load Resources; (f) Non-Spin available from Off-Line Generation Resources; (g) Non-Spin available from Resources with Output Schedules; (h) Undeployed Reg-Up and undeployed Reg-Down; (i) Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED; (j) Available capacity with Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED; (k) Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED; (l) Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED; and (m) The ERCOT-wide Physical Responsive Capability (PRC) calculated as follows: generationresourcei=onlineonlinegenerationAllresources PRC1 = Min(Max((RDF*HSL – Actual Net Telemetered Output)i , 0.0) , 0.2*RDF*HSLi) generationresourcei=onlineonlinegenerationAllresources PRC2 = ((Hydro-synchronous condenser output)i as qualified by item (6) of Operating Guide Section 2.3.1.2, Additionl Operational Details for Responsive Reserve Providers))   resources load online All resource load online i PRC3 = (RRS MW supplied from Load Resources)i PRC = PRC1 + PRC2 + PRC3 The above variables are defined as follows: Variable; Unit; Description. PRC1; MW; Generation On-Line greater than 0 MW. PRC2; MW; Hydro-synchronous condenser output. PRC3; MW; RRS supplied from Load Resources. PRC; MW; Physical Responsive Capability. RDF; The currently approved Reserve Discount Factor.

(2)	Each QSE shall operate Resources providing Ancillary Service capacity to meet its obligations.  If a QSE experiences temporary conditions where its total obligation for providing Ancillary Service cannot be met on the QSE’s Resources, then the QSE may add additional capability from other Resources that it represents.  It adds that capability by changing the Resource Status and updating the Ancillary Service Schedules and Ancillary Services Resource Responsibility of the affected Resources and notifying ERCOT under Section 6.4.8.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency.  If the QSE is unable to meet its total obligations to provide committed Ancillary Services capacity, the QSE shall notify ERCOT immediately of the expected duration of the QSE’s inability to meet its obligations.  ERCOT shall determine whether replacement Ancillary Services will be procured on behalf of the affected QSE according to Section 6.4.8.1.

- 6.5.9.4.2	EEA Levels

(1)	EEA Level 1 - Maintain a total of 2,300 MW of  PRC MW (Section 6.5.7.5, Ancillary Services Capacity Monitor).

(a)	ERCOT will:

(i)	Notify the Southwest Power Pool Security Coordinator;

(ii)	Initiate manual HRUC Dispatch Instructions to Generation Resources available and off-line that can perform within the expected timeframe of the emergency; and

(iii)	Use available DC Tie import capacity not already being used and inquire about availability of BLTs.

(b)	QSEs will notify ERCOT of any Resources uncommitted but available in the timeframe of the emergency.

(2)	EEA Level 2A - Maintain a total of 1,750 MW  of  PRC MW (Section 6.5.7.5).

(a)	In addition to the measures associated with EEA Level 1, ERCOT:

(i)	Will instruct TSPs and DSPs to reduce Customers’ Load by using distribution voltage reduction measures, if deemed beneficial by the TSP or DSP;

(ii)	Will instruct QSEs to deploy Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) in accordance with the following:

(A)	Instruct QSEs to deploy half of the Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 1 Load Resources providing Responsive Reserve.  QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from Group 2 if Load Resource operational considerations require such.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(B)	At the discretion of the ERCOT Operator, instruct QSEs to deploy the remaining Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 2 Load Resources providing Responsive Reserve. ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(C)	The ERCOT Operator may deploy both of the groups of Load Resources providing Responsive Reserves at the same time.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and

(D)	ERCOT shall post a list of Load Resources on the MIS Certified Area immediately following the DRUC for each QSE with a Load Resource obligation which may be deployed to interrupt under paragraph (A), Group 1 and paragraph (B), Group 2.  ERCOT shall develop a process for determining which individual Load Resource to place in Group 1 and which to place in Group 2.  ERCOT procedures shall select Group 1 and Group 2 based on a random sampling of individual Load Resources.  At ERCOT’s discretion, ERCOT may deploy all Load Resources at any given time during EEA Level 2A; and

(iii)	With the approval of the affected non-ERCOT Control Area, may instruct TSPs or DSPs to implement BLTs, which transfer Load from the ERCOT Control Area to non-ERCOT Control Areas.  Use of a BLT will be defined in the ERCOT Operating Guides.

(b)	Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

(3)	EEA Level 2B - Maintain system frequency at 60 Hz.  Following deployment of the measures associated with EEA Levels 1 and 2A, ERCOT will deploy available contracted EILS Loads, via a single VDI to the all-QSE Hotline as follows:

(a)	If less than 500 MW of EILS is available for deployment, ERCOT shall deploy all EILS Loads as a single block.

(b)	If the amount of EILS available for deployment equals or exceeds 500 MW, ERCOT may deploy EILS Loads as a single block or may deploy EILS Loads sequentially in two groups of approximately equal size as designated by ERCOT.  For a sequential group deployment, ERCOT shall instruct QSEs to deploy Group 1 immediately and to deploy Group 2 at a specified time in the future.  ERCOT shall develop a random selection methodology for determining which individual EILS Loads to place in Group 1 and which to place in Group 2, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to an EILS Contract Period, ERCOT shall notify QSEs representing EILS Loads of their EILS Loads’ Group assignments.

(c)	QSEs shall instruct the EILS Loads to curtail Load consistent with their commitments.

(d)	EILS may be deployed at any time in a Settlement Interval.

(e)	Once ERCOT has deployed EILS, EILS Loads shall remain reduced until ERCOT specifically releases the EILS deployment via a VDI to the all-QSE Hotline.

(f)	Unless scheduled to go Off-Line, due either to an EILS Time Period transition or a previously scheduled period of unavailability, an EILS Load deployed for EILS shall return to its committed operating level as soon as practical following an ERCOT recall.  All EILS Load shall return to normal within ten hours of being recalled.

(g)	Unless a media appeal is already in effect, ERCOT shall issue an appeal through the public news media for voluntary energy conservation.

(4)	EEA Level 3 - Maintain system frequency at 59.8 Hz or greater.

(a)	In addition to measures associated with EEA Levels 1, 2A and 2B, ERCOT will direct all TSPs and DSPs or their agents to shed firm Load, in 100 MW blocks, as documented in the ERCOT Operating Guides in order to maintain a steady state system frequency of 59.8 Hz.

(b)	In addition to measures associated with EEA Levels 1, 2A and 2B, TSPs and DSPs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs and DSPs shall not manually drop Load connected to under-frequency relays during the implementation of the EEA.