| PGRR Number | 003 | PGRR Title | New Planning Guide Section 9A, SSWG Procedure Manual |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | May 26, 2011 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Guide Section Requiring Revision |  | 9, Appendix A, Steady State Working Group Procedures Manual (new) |  |  |
| Revision Description |  | This Planning Guide Revision Request (PGRR) adds new Section 9, Appendices, Appendix A, Steady State Working Group Procedures Manual, to the Planning Guide. |  |  |
| Reason for Revision |  | This PGRR brings parts of the current Steady State Working Group Procedure Manual into the Planning Guide deemed to be appropriate for addition to the Planning Guide. |  |  |
| Overall Market Benefit |  | To be determined. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Procedural History |  | - On 11/23/10, PGRR003 was posted. - On 1/20/11, ERCOT comments were posted. - On 1/20/11, Oncor comments were posted. - On 1/21/11, the Planning Working Group (PLWG) considered PGRR003. - On 2/25/11, the PLWG again considered PGRR003. - On 3/25/11, the PLWG again considered PGRR003. - On 4/29/11, the PLWG again considered PGRR003. - On 5/25/11, Steady State Working Group (SSWG) comments were posted. - On 5/26/11, the PLWG again considered PGRR003 |  |  |
| PLWG Decision |  | On 1/21/11, the PLWG was in consensus to table PGRR003 for one month. On 2/25/11, the PLWG was in consensus to table PGRR003 for one month. On 3/25/11, the PLWG was in consensus to table PGRR003 for one month. On 4/29/11, the PLWG was in consensus to table PGRR003 for one month. On 5/26/11, the PLWG was in consensus to table PGRR003. |  |  |
| Summary of PLWG Discussion |  | On 1/21/11, it was stated that PGRR003 should be tabled until the options for Nodal Planning Go-Live have been resolved by the ERCOT Board. On 2/25/11, it was stated that PGRR003 should be tabled until the options for Nodal Planning Go-Live have been resolved by the ERCOT Board. On 3/25/11, it was suggested that PLWG table PGRR003 for an additional month to allow the SSWG to review and provide comments. ERCOT Staff suggested that an interim procedure should not be included in the Planning Guide and instead a formal procedure that is grey-boxed until a future effective date. On 4/29/11, it was noted that the SSWG is continuing their review of PGRR003 and committed to submitting comments prior to the May PLWG meeting. On 5/26/11, the 5/25/11 SSWG comments were discussed. Concern was expressed that the proposed changes incorporate detailed SSWG procedures not appropriate for the Planning Guide and that SSWG should refine the proposed language to eliminate non-binding activities. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 | Documentation of current SSWG process prior to Nodal Planning Go-Live. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Impact Area |
|  | 1 | None. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Impact Area |
|  | 1 | To be determined. | To be determined. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | None |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Wayne Kemper on behalf of the PLWG |
| E-mail Address | Wayne.kemper@centerpointenergy.com |
| Company | CenterPoint Energy |
| Phone Number | 713-207-2192 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 012011 | Proposed language changes to update the procedures to accurately reflect the actual process and also removed remaining zonal references. |
| Oncor 012011 | Proposed language changes to more accurately reflect current practices. |
| SSWG 052511 | Proposed language changes to reflect current case-building procedures; remove non-binding elements; and clarify existing practices. |

Proposed Guide Language Revision

ERCOT Planning Guide

Section 9:  Appendices

Appendix A:   Steady State Working Group Procedures Manual

mmmm, dd, yyyy

Table of Contents

###### SECTION 1.0 – Data Requirements

1.1 	General

1.2	Bus Data

1.3	Load Data

1.4	Generator Data

1.5	Line Data

1.6	Transformer Data

1.7	Static Reactive Devices

1.8	Dynamic Control Devices

###### HVDC Devices

###### SECTION 2.0 – Load-flow Procedures and Schedules

2.1	Data Set A Considerations

2.2	Data Set B Considerations

2.3	Error Screening and Case Updates

###### SECTION 3.0 – Other SSWG Activities

3.1	Transmission Loss Factor Calculation …

3.2	Contingency Database……………………………….........................................

###### SECTION 4.0 – Treatment of Mothballed Units in Planning

4.1	Planning Reserve Margin

4.2	Powerflow Base Cases

4.3	Alternative Dispatch Studies

###### SECTION 1.0 – Data Requirements

1.1 GENERAL

    - Model

- The network model submitted by the Transmission Service Provider (TSP) shall be in a format compatible with the latest approved PSS/E and rawd ASCII data format based on a 100 MVA base. The model should reflect expected system operation.

    - Data

The Steady State Working Group (SSWG) will use loads based upon the load data in the ERCOT Annual Load Data Request (ALDR) to build two sets of cases, Data Set A and Data Set B.

Data Set A consists of seasonal cases for the following year.  Data Set B consists of the following:

- Future summer peak planning cases

- A future minimum load planning case

After completion of the Data Set B cases, the following data will be updated by the SSWG:

- ERCOT Data Dictionary

- Updated Contingency List

1.2 BUS DATA

    - Areas defined by TSP

Each TSP is assigned a unique area name and number

    - Bus Data Records

All in-service transmission (60kV and above) and generator terminals shall be modeled in load-flow cases. Fixed reactive resources shall be modeled as a fixed component in the switchable shunt data record and not be part of the bus record.

    - Bus Ranges

Presently, ERCOT is modeled within a 100,000-bus range. The Chairman of the SSWG allocates bus ranges, new or amended, with confirmation from the SSWG members.  Bus ranges are based on high-side bus ownership.

Bus numbers from within the TSP’s designated bus range are assigned by the TSP and are to remain in the assigned ranges until the equipment or condition that it represents in the ERCOT load-flow cases changes or is removed.

    - Zone Ranges

Presently the Chairman of the SSWG allocates zone ranges, new or amended, with confirmation from SSWG members. Each TSP represents their network in the ERCOT load-flow cases using allocated zone ranges. Zone numbers that have been assigned by the TSP, within the TSP’s designated zone range, may be changed by the TSP as needed to represent their network in the ERCOT load-flow cases. Every zone number assigned must be from the TSP’s designated zone range.

    - Owner IDs

[Placeholder]

    - Bus Name

Electrical Bus names shall not identify the customers or owners of loads or generation at new buses unless requested by customers.  The twelve characters Electrical Bus Name representing individual transmission element in the planning model shall be unique and follow certain technical criteria as stated in the  Protocol Section 3.10, Network Operations Modeling and Telemetry.

1.3 LOAD DATA

Each bus modeling a load must contain at least one load data record.    All loads (MW and MVAr) should be modeled on the high side of transformers serving load at less than 60 kV.

Guidelines:

    - The bus number in the load data record must be a bus that exists in the base case. All self-serve loads must be identified by “SS”. If there are multiple self-serve loads at the same bus, then the self-serve loads will be identified by S1, S2, S3, etc.  Partial self-serve load should be modeled as a multiple load with “SS” identifying the self-serve portion. Distributed Generation must be identified by “DG” and modeled as negative load.

    - The load data record zone number must be in the zone range of the TSP serving the load.  It does not have to be the same zone that the bus is assigned to.

1.3.3	Generator auxiliary load should not be modeled at generating station buses.

1.3.4	In conformance to North American Electric Reliability Corporation (NERC) Reliability Standards and the ERCOT Operating GuidesEntities not having representation on SSWG shall submit the data to ERCOT or if the directly connected TSP has agreed to be the agent on SSWG for that Entity, to that TSP.  If load data is not timely submitted on the schedule and in the format defined by the TSP, then ERCOT shall calculate loads based on historical data and insert these loads into the power flow cases during DataSetA and DataSetB annual updates.

    - Multiple loads from different TSPs at a bus may be used. At this time, each TSP can define a load however it wishes with a load ID of its choice though careful coordination is required between TSP representatives to ensure that the loads at the bus get modeled correctly.

1.4 GENERATOR DATA

    - Acquisition of Generator Data

- Only net real and reactive generator outputs and ratings should be modeled in load-flow cases. Net generation is equal to the gross generation minus station auxiliaries and other internal power requirements.  All non-self-serve generation connected at 60kV and above with at least 10 MW aggregated at the point of interconnect must be explicitly modeled. A generator explicitly modeled must include generator step-up transformer and actual no-load tap position. Generation of less than 10 MW is still required to be modeled, but not explicitly.

- Unit Reactive Limits (URL) (leading and lagging) for existing units should be obtained from the most recent generator reactive unit test data provided by ERCOT. For units that have not been tested, limits will be obtained from the generator owner. URLs (leading and lagging) are tested at least once every two years. If the test does not meet these requirements, reference the ERCOT Operating Guides for further explanation or actions. Note that the Corrected Unit Reactive Limit (CURL) MVAr values are gross values at the generator terminals. Limited ERCOT Resource Asset Registration Form (RARF) data shall be made available to SSWG upon request.

- Generator reactive limits should be modeled by one value for Qmax and one value for Qmin as described below:

- Qmax

- Qmax is the maximum net lagging MVAr observed at the low side of the generator step up transformer when the unit is operating at its maximum net dependable MW capability.

- Qmin

- Qmin is the maximum leading MVAr observed at the low side of the generator step up transformer when the unit is operating at its maximum net dependable MW capability.

      - Self-Serve Generation

- Total self serve generation MWs shall match total self-serve load MWs.

      - Coordination with other ERCOT Working Groups

- All generator data should be coordinated with the Dynamics Working Group (DWG), Operations Working Group (OWG), Network Data Support Working Group (NDSWG) and System Protection Working Group (SPWG) members to assure that it is correct before submitting the cases. This will insure that all of the cases have the most current steady state and dynamics information.  The following are items from the fall peak SSWG case that should be provided to these working groups for annual coordination by the end of the year:

- Unit bus number

- Unit ID

- Unit maximum and minimum real power capabilities

- Unit maximum and minimum reactive power capabilities

- Unit MVA base

- Resistive and reactive machine impedances

- Resistive and reactive Generator Step-Up (GSU) transformer impedances

    - Generation Dispatch Methodology

In order to simulate the future market, the following methodology for generation dispatch has been adopted for building the Data Set A and Data Set B power flow cases.

Existing and planned units owned by the Non-Opt-In Entities (NOIE) are dispatched according to the NOIE's planning departments; unless a NOIE requests that their units are to be dispatched according to the order that is described below.

Private network generation is also dispatched independently. The plants are dispatched to meet their load modeled in the case. DC Ties are modeled as load levels or at generation levels based on historical data.  Likewise, wind plants are modeled at generation levels based on historical data.

Units that are solely for black start purposes are to be modeled in the base cases; however, these units should not be dispatched.  Black Start units are designated with a unit ID that begins with the letter ‘B’ which can be followed by an alphanumeric character (for example, ‘B1’, ‘B2’, etc.).

All other units are dispatched by performing a system simulation using the UPLAN software package.  The UPLAN simulation will dispatch units in order to minimize production costs taking into account unit start-up times and cost and heat rates while adhering to the following guidelines for each set of cases:

Data Set A cases are dispatched to maintain Commercially Significant Constraints (CSCs) and Closely Related Elements (CRE) loading below their limits.  The Uplan software simulates the system load for the two weeks leading up to the peak hour for each season.

Data set B economically constrained cases are dispatched in the most economical way for a given load level with no consideration for overloads.  The Uplan software  simulates the system load for the two weeks leading up to the peak hour for each summer peak case and the two weeks leading up to the minimum load hour for the minimum case.

In all cases spinning reserve is maintained according to the ERCOT Operating Guides.  Mothballed units are treated as described in Appendix A, Section 4.0, Treatment of Mothballed Units in Planning.  The dispatch may be modified for Data Set A cases if necessary to maintain voltages at acceptable levels.

New Generation Resources will be included in the base cases once ERCOT receives an executed interconnection agreement and is notified by the TSP that a complete financially-binding Notice to Proceed between the generator and TSP has been executed or ERCOT receives a commitment letter from a Municipally Owned Utility (MOU) or an Electric Cooperative (EC) building a generation project.

SSWG shall be able to review and modify the generation dispatch based on historical information.

Extraordinary Dispatch Conditions

These differences can result in future cases without sufficient dispatchable generation resources to match load.  When such a condition is encountered in future cases, ERCOT may increase generation resources by taking the indicated action, or adding generation, in the following order:

- Direct Current(DC) Ties dispatched to increase transfers into ERCOT to the full capacity of the DC Ties.

- Mothballed units that have not announced their return to service.

- Ignore spinning reserve.

- Increase NOIE generation with prior NOIE consent

- Add publicly announced plants without interconnect agreements.

- Black Start Units

- Add Generation Resources at the sites of retired units.

    - Voltage Profile Adjustments

[Placeholder]

- 1.5 LINE DATA

    - Use of Load-flow Data Fields

      - Bus Specifications

      - Circuit (Branch) Identifier

Circuit identifiers are limited to two alphanumeric characters.  Each TSP will determine its own naming convention. These identifiers are typically numeric values (e.g. 1 or 2) that indicate the number of branches between two common buses, but many exceptions exist.

      - Impedance Data

The resistive and reactive impedance data contained in the load-flow cases are both expressed in per-unit quantities that are calculated from a base impedance. The base impedance for transmission lines is calculated from the system base MVA and the base voltage of the transmission branch of interest.  The system base MVA used in the ERCOT load-flow cases is 100 MVA (S = 100 MVA).  The base voltage for a transmission line branch is the nominal line-to-line voltage of that particular transmission branch

        - Charging

Line charging is expressed as total branch charging susceptance in per unit on the 100 MVA system base.  The total branch charging is expressed in MVARs and divided by the system base MVA to get per unit charging.

      - Facility Ratings

ERCOT load-flow cases contain fields for three ratings for each branch record.  The ratings associated with these three fields are commonly referred to as Rate A, Rate B and Rate C.  Following are the ERCOT facility ratings definitions:

        - Ratings Definitions

Rate A – Normal Rating

Continuous Rating:  Represents the continuous MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer (MLSE) at the applicable ambient temperature.   The Transmission Facility can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

Rate B – Emergency Rating

Emergency Rating:  Represents the two hour MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer (MLSE) at the applicable ambient temperature.  The Transmission Facility can operate at this rating for two hours without violation of NESC clearances or equipment failure.

Rate C – Conductor/Transformer Rating

Emergency Rating of the Conductor or Transformer:  Represents the two hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The conductor or transformer can operate at this rating for two hours without violation of NESC clearances or equipment failure.

I.e. Rate C ≥ Rate B ≥ Rate A

      - Status

Entities are allowed to submit branch data with an out-of-service status for equipment normally out of service.

      - Line Length and Ownership

The line length will be submitted by the TSP’s during the DSA and DSB case creation and TPIT updates and ownership may be submitted at their discretion.

        - Line Length

This data will be provided in miles

    - Coordination of Tie Lines

Careful coordination and discussion is required among SSWG members to verify all modeled tie-line data.

    - Metering Point

Each tie line or branch must have a designated metering point and this designation should also be coordinated between neighboring TSP areas.

1.6 TRANSFORMER DATA

    - Transformer Data

Every transformer is to be represented in the transformer data record block.  Both two winding transformers and three winding transformers can be specified in the transformer data record block. Three-winding transformer should be represented by its three-winding model and not by its equivalent two-winding models.

      - Bus Numbers

      - Transformer Circuit Identifier

Where practical, TO’s should identify autotransformers with the letter A as the first character of the ID field.  GSU transformers should be identified with the letter G.  Phase-shifting transformers should be identified with the letter P.

      - Impedance Data

The resistance and reactance data for transformers in the power flow database are specified: (1) in per-unit on 100 MVA system base (default), (2) in per-unit on winding base MVA and winding bus base voltage, (3) in transformer load loss in watts and impedance magnitude in per-unit on winding base MVA and winding bus base voltage.

        - Resistance

Transformer test records should be used to calculate the resistance associated with a transformer branch record. Where transformer test records are unavailable, the resistance should be entered as zero.

        - Reactance

Transformer test records or transformer nameplate impedance should be used to calculate the reactance associated with a transformer branch record. Where the transformer resistance component is known, the transformer impedance is calculated on the same base using the known data and the reactance component is determined using the Pythagorean Theorem. Where the transformer resistance is assumed to be zero, the calculated transformer impedance can be assumed to be equal to the transformer reactance.

        - Susceptance

For load-flow modeling purposes, the transformer susceptance is always assumed to be zero.

      - Transformer Ratings

The ratings used for transformer branches are defined the same as in Appendix A, Section 1.5.1.4, Facility Ratings, above.

1.7 STATIC REACTIVE DEVICES

Presently all shunt reactors and capacitors that are used to control voltage at the transmission level are to be modeled in the ERCOT load-flow cases to simulate actual transmission operation.

    - Switched Shunt Devices

      - Bus Shunt

A shunt capacitor or reactor connected to the high side or low side of a substation transformer in a substation should be represented in the ERCOT load-flow case as a switched or fixed shunt device to accurately simulate operating conditions.

The FACTS model figure has a series element that is connected between two buses and a shunt element that is connected between the sending end bus and ground. The shunt element at the sending end bus is used to hold the sending end bus voltage magnitude to VSET subject to the sending end shunt current limit SHMX.  This is handled in power flow solutions in a manner similar to that of locally controlling synchronous condensers and continuous switched shunts.  One or both of these elements may be used depending upon the type of device.

A unified power flow controller (UPFC) has both the series and shunt elements active, and allows for the exchange of active power between the two elements. (

###### SECTION 2.0 – Load-Flow Procedures and Schedules

2.1 DATA SET A CONSIDERATIONS

    - Data Set A Uses

Data Set A cases are submitted by the ERCOT region in response to FERC 715 requirements and are posted on ERCOT web site for general use.

    - Data Set A Case Definitions

Load-flow cases produced by ESP are to be divided into two groups.  The first group, “Data Set A,” models expected conditions for the following year’s four seasons (eight cases).  The second group, “Data Set B,” models cases for the five-year planning horizon.

Data Set A seasons are as follows:

SPG		March, April, May

SUM		June, July, August, September

FAL		October, November

WIN		December, January, February

ERCOT DATA SET A BASECASES

(YR) = FOLLOWING YEAR

| BASE CASE | # NOTES | TRANSMISSION IN-SERVICE DATE |
| --- | --- | --- |
| (YR) SPG1 | 2 | April 1, (YR) |
| (YR) SPG2 | 3 | April 1, (YR) |
| (YR) SUM1 | 1 | July 1, (YR) |
| (YR) SUM2 | 3 | July 1, (YR) |
| (YR) FAL1 | 2 | October 1, (YR) |
| (YR) FAL2 | 3 | October 1, (YR) |
| (YR+1) WIN1 | 1 | January 1, (YR+1) |
| (YR+1) WIN2 | 3 | January 1, (YR+1) |

## Notes

- Cases to represent the maximum expected load during the season.

- Cases to represent maximum expected load during month of transmission in-service date.

- Cases to represent lowest load on same day as the corresponding seasonal case (not a minimum case). For example, (YR) FAL2 case represents the lowest load on the same day as the (YR) FAL1 case.

    - Entity Responsibilities

The Data Set A load-flow cases are assembled and produced by ESP.  The responsibilities for providing this data are divided among the various market participants. These data provision responsibilities may overlap among the various market participants because participants may designate their representative or a participant may be a member of more than one market participant group.  The market participants can generally be divided into four groups: TSPs, Load Serving Entities (LSEs), Power Generation Companies, and Market Entities.  The data responsibilities of each group are as follows:

      - TSPs

It is the responsibility of the TSPs to provide all the data required to model the transmission system (line impedances, ratings, transformers, reactive sources, etc.) This will include data for all generator step-up transformers physically tied to the system of the TSP.  TSPs shall model the load or generation data if they are the designated representatives for load entities or power generating companies.

      - Load Serving Entities

Each ERCOT Distribution Service Provider (DSP) directly interconnected with the transmission system (or its agent so designated to ERCOT) shall provide annual load forecasts to the ERCOT as outlined in the ERCOT Annual Load Data Request (ALDR) Procedures.  For each substation not owned by either a TSP or a DSP, the owner shall provide a substation load forecast to the directly connected TSP sufficient to allow it to adequately include that substation in its ALDR response.  Entities not having representation on SSWG shall submit the data to ERCOT or if the directly connected TSP has agreed to be the agent on SSWG for that entity, to that TSP.  If load data is not timely submitted on the schedule and in the format defined by the TSP, then ERCOT shall calculate loads based on historical data and insert these loads into the power flow cases during DataSetA and DataSetB annual updates.

      - Power Generating Companies

It is the responsibility of the generation entities to provide all data required to model the generators in all the cases. (See Appendix A) Section 1.4. This data should be coordinated with ERCOT and should include but is not limited to unit capabilities.

      - Marketing Entities

It is the responsibility of marketers to supply the load and/or generation data if they are the designated representatives for either a load or generating entity or both.

2.2 DATA SET B CONSIDERATIONS

    - Data Set Uses

    - Data Set B Case Definitions

ERCOT DATA SET B BASECASES

(YR) = FOLLOWING YEAR

| BASE CASE | # NOTES | TRANSMISSION IN-SERVICE DATE |
| --- | --- | --- |
| (YR+1) SUM1 | 1 | JULY 1, (YR+1) |
| (YR+2) SUM1 | 1 | JULY 1, (YR+2) |
| (YR+3) MIN | 2 | JANUARY 1, (YR+3) |
| (YR+3) SUM1 | 1 | JULY 1, (YR+3) |
| (YR+4) SUM1 | 1 | JULY 1, (YR+4) |
| (YR+5) SUM1 | 1 | JULY 1, (YR+5) |

## Notes

- Cases to represent the maximum expected load during the season.

- Cases to represent the absolute minimum load expected for (YR+3).

    - Data Set B Dispatching

Data Set B will contain economically dispatched generation (ECO).

    - ERCOT Data Dictionary

Each SSWG member will submit a data file listing all buses that exist in any case from either Data Set A or B 30 days after completion of Data Set B cases.  This file is called the ERCOT Data Dictionary.   The data dictionary is used by ESP to show correlation between base case bus numbers and TSP area SCADA names.  Also, the data dictionary without the SCADA names is included as part of ERCOT’s FERC 715 filing.

2.3 ERROR SCREENING AND CASE UPDATES

    - Solved Case Checks

# Case Updates

When necessary the TSP will document updates, which will be posted by ESP. The file name should have a clear description, which will include provider’s acronym and the specific case to be updated.

SECTION 3.0 – Other SSWG Activities

3.1 TRANSMISSION LOSS FACTOR CALCULATIONS

Transmission Loss Factors

The transmission loss factors must be calculated according to Protocol Section 13. The loss factors are calculated using SSWG DSA base cases.

3.2	Planning-Related Contingency Database

Contingency Procedure:

- All the TO’s either submit the contingencies individually or will updated the existing database.

- The duplicate contingencies are included only once and are attributed to the TO which comes first in alphabetical order.

- All contingencies need to be categorized based on NERC categories.

- Current contingency database is sent to all TSP’s for reviewing.

- ERCOT will update the contingency database when a TSP submits the contingency changes related to a major Topology change ( - incremental change).Every time the database changes, files in MUST, PSS/E, Powerworld, UPLAN and VSAT formats are posted online.

- Detailed instructions can be found on the Planning and Operations Information website at ercot.com.

AEP’s transmission lines can operate at the emergency ratings for 1000 hours over the life of the conductor before the loss of strength will cause unacceptable sag conditions.  In accordance with this procedure manual, The Emergency Rating represents a 2-hour rating.  Operations must take action to reduce the flows below the

SECTION 4.0 – Treatment of Mothballed Units in Planning

The treatment described in this paper was developed by a joint workgroup of the Wholesale Market Subcommittee (WMS) and the Reliability and Operations Subcommittee (ROS) at the direction of the Technical Advisory Committee (TAC).

4.1 Planning Reserve Margin

The ERCOT-wide reserve margin for assessing generation adequacy will continue to be calculated as recommended by the Generation Adequacy Task Force and approved by TAC in early 2003.  However, for the purpose of determining how mothballed units will be treated in the powerflow cases, an alternative reserve margin calculation will be performed.  In this alternative calculation, the capacity of mothballed units that have given sufficiently firm indication that they will return to service by a specified year will be included in the reserve calculation for that year and thereafter.  However, the capacity of all mothballed units that have not given such indication will not be included in the calculation for any year.  From this alternative reserve margin calculation, the year in which the ERCOT reserve margin drops below the target of 12.5% will be determined and will trigger the inclusion of the remaining mothballed units in the powerflow cases.

4.2 Powerflow Base Cases

Powerflow Base Cases

In the first year that has a reserve margin less than 12.5%, based on the alternative reserve margin calculation described above, the mothballed units that have not committed to a specific un-mothballing date will be made available to meet the load requirement that is not able to be met by operational and planned generating units and imports (as included in the Capacity section of the CDR) in the powerflow base cases.   However, in order to minimize the effect on transmission plans of the decision to use mothballed units to meet the load requirement, the generation that is needed from mothballed units as a group will be allocated over all the mothballed units on a capacity ratio share basis.  If this technique results in some of the mothballed units being dispatched at a level below their minimum load, an economic ranking will be used to remove the least economic units from consideration for that particular case so that the allocation of the load requirement among the remaining mothballed units will result in all of those units being loaded above their minimum loads.

For example, assume that, in some future year, ERCOT has a projected peak demand of 80,000MW and installed capacity of 82,000MW with 3000MW of that installed capacity being units that are mothballed and have not indicated they will return.  For this simple example, assume that the mothballed capacity is 20 generating units of equal 150MW size.  Ignoring losses, the powerflow case would need to include 1000MW of the 3000MW mothballed capacity in order to match the load.   Thus, each of the 20 mothballed units would be set to an output of 50MW in the powerflow case (assuming their minimum load is less than 50MW).

4.3 Alternative Dispatch Studies

Alternative Dispatch Studies

While this treatment of mothballed units attempts to generally minimize the effect of the assumption that mothballed units will be used to meet the load requirement in the powerflow cases (rather than assumed new generation), the planning process should also consider alternative generation dispatches in instances where this treatment of mothballed units could have a direct effect on transmission plans.  Specifically, in instances where having a mothballed unit available would alleviate the need for a transmission project that would be required to meet reliability criteria if the mothballed unit were not to return, the transmission project should not be deferred based on the assumption that the mothballed unit will return to service.

- The 2008 % Capacity Factor data is below.