| NPRR Number | 356 | NPRR Title | EEA Changes Related to Dispatch Instructions and BLTs |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | July 7, 2011 |  |  |
| Proposed Effective Date |  | September 1, 2011 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Protocol Sections Requiring Revision |  | 6.5.9.4.1, General Procedures Prior to EEA Operations 6.5.9.4.2, EEA Levels |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) changes the need to issue Dispatch Instructions to suspend any ongoing ERCOT-required generating unit or Resource performance testing and moves the requirement to inquire about the availability of Block Load Transfers (BLTs) from Energy Emergency Alert (EEA) Level 2A to EEA Level 2B. |  |  |
| Reason for Revision |  | The changes to the EEA process will allow ERCOT to be more efficient in making Hotline calls to Qualified Scheduling Entities (QSEs). |  |  |
| Overall Market Benefit |  | Removing instructions from ERCOT procedures and adding them to the Protocols will reduce the time it takes to make Hotline calls and will improve Market Participant response time. |  |  |
| Overall Market Impact |  | Unknown. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR356 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 5/4/11, NPRR356 and the associated Impact Analysis were posted. - On 5/17/11, ROS comments were posted. - On 5/18/11, Operations Working Group (OWG) comments were posted. - On 5/19/11, PRS considered NPRR356. - On 6/23/11, PRS considered the 5/19/11 PRS Report and Impact Analysis for NPRR356. - On 7/7/11, TAC considered NPRR356. |  |  |
| PRS Decision |  | On 5/19/11, PRS unanimously voted to recommend approval of NPRR356 as amended by the 5/18/11 OWG comments and as revised by PRS. All Market Segments were present for the vote. On 6/23/11, PRS voted to endorse and forward the 5/19/11 PRS Report and Impact Analysis for NPRR356 to TAC. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 5/19/11, ERCOT Staff suggested administrative revisions for PRS consideration. On 6/23/11, there was no discussion. |  |  |
| TAC Decision |  | On 7/7/11, TAC unanimously voted to recommend approval of NPRR356 as recommended by PRS in the 6/23/11 PRS Report. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 7/7/11, there was no discussion. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Unknown. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Removing instructions from ERCOT procedures and adding them into the Protocols will reduce the time it takes to make Hotline calls and will improve Market Participant response time. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Colleen Frosch |
| E-mail Address | cfrosch@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4219 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ROS 051711 | Endorsed NPRR356 as submitted and requested that OWG review and provide comments, if necessary. |
| OWG 051811 | Endorsed NPRR356 as revised by OWG. |

Comments

Please note that the following NPRRs also propose revisions to Section 6.5.9.4.2 which is also included within this NPRR:

- NPRR362, Changes to PRC Calculation

- NPRR379, EILS Dispatch Sequence and Performance Criteria Upgrades

Proposed Protocol Language Revision

- 6.5.9.4.1	General Procedures Prior to EEA Operations

Prior to declaring EEA Level 1 detailed in Section 6.5.9.4.2, EEA Levels, ERCOT may perform the following operations consistent with Good Utility Practice:

(a)	Provide Dispatch Instructions to QSEs for specific Resources to operate at an Emergency Base Point to maximize Resource deployment so as to increase Responsive Reserve levels on other Resources;

(b)	Commit specific available Resources as necessary that can respond in the timeframe of the emergency.  Such commitments will be settled using the HRUC process;

(c)	Start RMR Units available in the time frame of the emergency.  RMR Units should be loaded to full capability;

(d)	Utilize available Resources providing Non-Spin services as required; and

(e)	ERCOT shall use the PRC to determine the appropriate emergency Notification and EEA levels.

- 6.5.9.4.2	EEA Levels

(1)	EEA Level 1 - Maintain a sum total of 2,300 MW that results from adding the amount of ERCOT PRC MW (Section 6.5.7.5, Ancillary Services Capacity Monitor) and the amount of RRS MW which is supplied from Load Resources.

(a)	ERCOT shall:

(i)	Notify the Southwest Power Pool Reliability Coordinator;

(ii)	Request available Generation Resources, that can perform within the expected timeframe of the emergency, to come On-Line by initiating manual HRUC or through Dispatch Instruction;

(iii)	Use available DC Tie import capacity not already being used; and

(iv)	Issue a Dispatch Instruction for Resources to remain On-Line which, before start of emergency, were scheduled to come Off-Line.

(b)	QSEs shall:

(i)	Ensure COPs and telemetered HSLs are updated and reflect all Resource delays and limitations; and

(ii)	Suspend any ongoing ERCOT required Resource performing testing.

(2)	EEA Level 2A - Maintain a sum total of 1,750 MW that results from adding the amount of ERCOT PRC MW (Section 6.5.7.5) and the amount of RRS MW which is supplied from Load Resources.

(a)	In addition to the measures associated with EEA Level 1, ERCOT shall:

(i)	Instruct TSPs and DSPs or their agents to reduce Customers’ Load by using distribution voltage reduction measures, if deemed beneficial by the TSP, DSP, or their agents;

(ii)	Instruct QSEs to deploy all Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) in accordance with the following:

(A)	Instruct QSEs to deploy half of the Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 1 Load Resources providing Responsive Reserve.  QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from Group 2 if Load Resource operational considerations require such.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(B)	At the discretion of the ERCOT Operator, instruct QSEs to deploy the remaining Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 2 Load Resources providing Responsive Reserve. ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(C)	The ERCOT Operator may deploy both of the groups of Load Resources providing Responsive Reserves at the same time.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and

(D)	ERCOT shall post a list of Load Resources on the MIS Certified Area immediately following the DRUC for each QSE with a Load Resource obligation which may be deployed to interrupt under paragraph (A), Group 1 and paragraph (B), Group 2.  ERCOT shall develop a process for determining which individual Load Resource to place in Group 1 and which to place in Group 2.  ERCOT procedures shall select Group 1 and Group 2 based on a random sampling of individual Load Resources.  At ERCOT’s discretion, ERCOT may deploy all Load Resources at any given time during EEA Level 2A.

(b)	Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

(3)	EEA Level 2B - Maintain system frequency at 60 Hz.  Following deployment of the measures associated with EEA Levels 1 and 2A.

(a)	 ERCOT will deploy available contracted EILS Loads, via a single VDI to the all-QSE Hotline as follows:

(i)	If less than 500 MW of EILS is available for deployment, ERCOT shall deploy all EILS Loads as a single block.

(ii)	If the amount of EILS available for deployment equals or exceeds 500 MW, ERCOT may deploy EILS Loads as a single block or may deploy EILS Loads sequentially in two groups of approximately equal size as designated by ERCOT.  For a sequential group deployment, ERCOT shall instruct QSEs to deploy Group 1 immediately and to deploy Group 2 at a specified time in the future.  ERCOT shall develop a random selection methodology for determining which individual EILS Loads to place in Group 1 and which to place in Group 2, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to an EILS Contract Period ERCOT shall notify QSEs representing EILS Loads of their EILS Loads’ Group assignments.

(iii)	QSEs shall instruct the EILS Loads to curtail Load consistent with their commitments.

(iv)	EILS may be deployed at any time in a Settlement Interval.

(v)	Once ERCOT has deployed EILS, EILS Loads shall remain reduced until ERCOT specifically releases the EILS deployment via a VDI to the all-QSE Hotline.

(vi)	Unless scheduled to go Off-Line, due either to an EILS Time Period transition or a previously scheduled period of unavailability, an EILS Load deployed for EILS shall return to its committed operating level as soon as practical following an ERCOT recall.  All EILS Load shall return to normal within ten hours of being recalled.

(b)	Unless a media appeal is already in effect, ERCOT shall issue an appeal through the public news media for voluntary energy conservation.

(c)	With the approval of the affected non-ERCOT Control Area, TSPs, DSPs or their agents may implement BLTs, which transfer Load from the ERCOT Control Area to non-ERCOT Control Areas in accordance with BLTs as defined in the Operating Guides.

(4)	EEA Level 3 - Maintain system frequency at 59.8 Hz or greater.

(a)	In addition to measures associated with EEA Levels 1, 2A and 2B, ERCOT will direct all TSPs and DSPs or their agents to shed firm load, in 100 MW blocks, as documented in the Operating Guides in order to maintain a steady state system frequency of 59.8 Hz.

(b)	In addition to measures associated with EEA Levels 1, 2A and 2B, TSPs and DSPs or their agents will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs and DSPs or their agents shall not manually drop load connected to under-frequency relays during the implementation of the EEA.