## Slide 1: Operations/Planning Case Consistency 2011 Base Case Cycle
PLWG presentation to ROS
March 10, 2011

## Slide 2: 2011 SSWG Case Consistency Requirements
Develop Planning/Operations Case consistency metrics that meet, as closely as achievable, Nodal Protocol 3.10.2 and similarly, the TAC approved “Principles of Consistency” for use in the 2011 cycle of case building.
List specific modeling issues that depart from the “Principles of Consistency” due to:
  Topology Processor deficiencies (e.g. BC/BO identifiers)
  Topology Processor model detail design (e.g. Low Voltage networks, Asynchronous ties)
  Possible additional differences as discovered in the case building process.
TSPs to meet tolerance threshold within the “different numerical precision” criteria
  R, X and B, each within a tolerance of 0.0002 per unit
  Rating A & B within 1 MVA
Excerpt from Nodal Protocol 3.10.2:
“….ERCOT shall develop models for annual planning purposes that contain, as much as practicable, information consistent with the Network Operations Model.”
Excerpt from Principles of Consistency document:
“All existing transmission line’s and tranformer’s impedances (or equivalent branch circuit impedance) and ratings (Normal,Emergency and 15-minute, if modeled) shall be identical”…
“(”Identical” as used herein permits only those differences due to the use of different numerical precision)”

## Slide 3: 2011 SSWG Case Consistency Requirements
Topology Processor Deficiencies: The Topology Processor assigns an ID of BC or BO to very short lines, including bus ties, instead of the assigned circuit ID.
  This issue only impacts reconciliation efforts, however, given that the “to bus” and “from bus” are properly identified, the users of the models will still be able to reconcile lines, with the exception of the potential instance of multiple tie/very short lines in-parallel. This issue will be resolved as a part of SCR760.
Topology Processor model detail design.
  The NMMS database only includes high voltage AC data, however, SSWG cases include low voltage networks and asynchronous ties.
  Buses that are common to both models will be identical, therefore, the high voltage bus associated with these facilities will be identical
  There were no mentioned plans to expand NMMS to match database needs
  Possible additional differences as discovered in the case building process. This is the first attempt to build a “matching” case, and there may be additional discovered deficiencies in the Topology Processor.

## Slide 4: Impedance & Ratings Comparison
New Date Set A case comparison, performed by ERCOT, shows a large number of ratings and impedance differences.
Data Set A cases to be completed by August 1, 2011, therefore, significant resource commitment by TSPs required to submit NOMCRs with consideration of 90-day NOMCR lead-time (due April 30).
In the current state, approximately 80% of elements are common to both models. The comparison above considers only elements common to both models.
ERCOT Case Comparison using TP-Mirror Cases, March 8, 2011.

## Slide 5: RARF Data Submission
A contributor to case differences will be related to generation resources and Private Use Network (PUN) data that is submitted through RARF.
Process to incorporate RARF data into Operations and Planning Model:
Resource and PUN data is submitted by the facility owner, directly to ERCOT.
ERCOT validates the data, corresponding with facility owner as needed.
ERCOT develops NOMCR and PMCR for entry into NMMS database resulting in a change to the Operations and Planning models
ERCOT informs “footprint” TSP of model changes via e-mail.
If, upon TSP review, there is a disagreement concerning the validity of data, ERCOT will coordinate with all entities involved and bring issue to resolution.

## Slide 6: Recommended Action Items
During the 2011 SSWG base case building cycle, TSPs will develop cases that, when compared to the same time-frame snapshot Operations case, will:
Have identical connectivity of all high voltage busses and their high voltage connecting facilities.
Have impedances within 0.0002 per unit of all common facilities. Impedance measure applied to R, X and B.
Have ratings within 1 MVA on all common facilities.
Have identical bus numbers and circuit IDs with the exception of the BC/BO branch identifier.
Possibly have other necessary differences as discovered in the case building process, to be vetted through the PLWG. Differences must be required to maintain planning functionality.