## Slide 1: PDCWG Report to ROS
March 10, 2011
Sydney Niemeyer

## Slide 2
CPS1 = 136.44

## Slide 3
April 17, 2006
February 2, 2011

## Slide 6
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 149.74

## Slide 7
CPS 2 92.22

## Slide 9: Two Part Analysis
Calculation of Interconnection Frequency Response.
  At the lowest frequency point during the first 20 seconds to determine frequency response available to prevent UFLS.
  At the average Point B settling frequency.
    Is the settling frequency lower than Point C?
    Is the settling frequency stable and gradually returning to schedule?
      Secondary generator runbacks or trips?
      Primary Frequency response not sustained?
      Grid load increase?
Calculation of frequency rate of change per MW of grid imbalance in µHz/second/MW lost.
  The more negative the frequency rate of change per MW of generation lost indicates lower grid inertia.
  Lower grid inertia provides less time to deliver Primary Frequency Response from generators.
  Total Energy, available spinning reserve and total wind generation is provided to give possible causes for the low grid inertia.

## Slide 10: Frequency Events Reviewed
Friday Jan 28, 2011 @ 13:01
  325 MW -557 MW/0.1 Hz 85% of Bias -117 µHz/sec/MWloss
Saturday Jan 29, 2011 @ 22:29
  532 MW -435 MW/0.1 Hz 67% of Bias -99.6 µHz/sec/MWloss
Tuesday Feb 1, 2011 @ 22:27
  593 MW -589 MW/0.1 Hz 90% of Bias -69.7 µHz/sec/MWloss
Wednesday Feb 2, 2011 @ 02:18
  717 MW -453 MW/0.1 Hz 69% of Bias -79.5 µHz/sec/MWloss
Wednesday Feb 2, 2011 @ 05:14
  146 MW -347 MW/0.1 Hz 53% of Bias -not available
Wednesday Feb 2, 2011 @ 05:39
  520 MW -417 MW/0.1 Hz 64% of Bias -71.2 µHz/sec/MWloss
Wednesday Feb 2, 2011 @ 08:24
  776 MW -414 MW/0.1 Hz 63% of Bias -69.6 µHz/sec/MWloss
Wednesday Feb 2, 2011 @ 10:55
  841 MW -444 MW/0.1 Hz 68% of Bias -72.5 µHz/sec/MWloss

## Slide 11: Frequency Events Reviewed
Wednesday Feb 9, 2011 @ 13:01
  582 MW -511 MW/0.1 Hz 78% of Bias -72.2 µHz/sec/MWloss
Tuesday Feb 15, 2011 @ 16:40
  770 MW -357 MW/0.1 Hz 55% of Bias -111.7 µHz/sec/MWloss
Wednesday Feb 16, 2011 @ 09:25
  602 MW -306 MW/0.1 Hz 47% of Bias -116.4 µHz/sec/MWloss

## Slide 14
The Generator that caused the frequency deviation recovered beginning 22:30:10. Average period was shortened to capture frequency response only during the appropriate time period.

## Slide 15
Frequency Rate of Change Hz/second
-99.6 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 17
Frequency Rate of Change Hz/second
-69.7 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 19
Frequency Rate of Change Hz/second
-114.6 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 21
No high speed data available for this small event of 145 MW tripping. Further frequency decay following trip. Additional RRS was deployed.

## Slide 23
Frequency Rate of Change Hz/second
-71.0 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 27
Frequency Rate of Change Hz/second
-72.5 µ Hz/second/MW Tripped (more negative number indicates less grid inertia)

## Slide 34: Event Summary
Lowest inertia event Jan 28, -117 µ Hz/second/MW lost and Feb 16, -116 µ Hz/second/MW lost.
Lowest Primary frequency response:
  At Point C for UFLS protection -278 MW/0.1 Hz Feb 15.
  At Point B for sustained response -306 MW/0.1 Hz Feb 16.
The PDCWG asked ERCOT to validate HSL and spinning reserve data on several events to confirm expected primary frequency response expectations. This will be completed by checking data and contacting the Resource in question.

## Slide 35: Next PDCWG Meeting
March 30, 2011 at the Met Center.